## 6B - Great Falls, MT
Versioning Information |  |  | GCR Tradeoffs
Building Category | Commercial |  | GCR | Title Angle | Performance (kWh/kW) | GCR Losses (%) | Roof Array Size (kW) | Roof Array Production (kWh)
Building Type | Medium Office |  | 0.1 | 10% | 1272.56 | 0% | 22.0422 | 28049.9618
Code/Year | ASHRAE 90.1-2019 |  | 0.2 | 10% | 1272.06 | 0.03929% | 44.0843 | 56077.8815
Location | Great Falls, MT |  | 0.3 | 10% | 1271.42 | 0.08958% | 66.1265 | 84074.5013
EnergyPlus Version | 9.5.0 |  | 0.4 | 10% | 1270.57 | 0.1564% | 88.1686 | 112024.3917
SAM Version | 2020.11.29 r2 |  | 0.5 | 10% | 1269.28 | 0.2577% | 110.2108 | 139888.3177
|  |  | 0.6 | 10% | 1267.13 | 0.4267% | 132.2529 | 167581.6375
Building Roof Constraints |  |  | 0.7 | 10% | 1262.18 | 0.8157% | 154.2951 | 194748.1499
Roof Width | 49.9262 | m | 0.8 | 10% | 1248.26 | 1.91% | 176.3372 | 220114.7
Roof Length | 33.2842 | m | 0.9 | 10% | 1219.41 | 4.177% | 198.3794 | 241905.7926
Required Setback | 1.8288 | m | 0.1 | 20% | 1360.77 | 0% | 22.0422 | 29994.3001
Reserve for HVAC | 0.2 | fraction | 0.2 | 20% | 1358.74 | 0.1492% | 44.0843 | 59899.1091
Roof Area for PV | 1096.6245 | m² | 0.3 | 20% | 1356.18 | 0.3373% | 66.1265 | 89679.3798
|  |  | 0.4 | 20% | 1352.08 | 0.6386% | 88.1686 | 119211.0152
PV Parameters |  |  | 0.5 | 20% | 1345.88 | 1.094% | 110.2108 | 148330.4622
Nominal Efficiency | 20.1% |  | 0.6 | 20% | 1332.38 | 2.086% | 132.2529 | 176211.1403
Nominal Irradiance | 1000 | W/m² | 0.7 | 20% | 1309.5 | 3.768% | 154.2951 | 202049.3925
|  |  | 0.8 | 20% | 1276.87 | 6.166% | 176.3372 | 225159.7079
Roof Array Design |  |  | 0.9 | 20% | 1230.86 | 9.547% | 198.3794 | 244177.2364
Selected Tilt | 10% |  | 0.1 | 30% | 1411.67 | 0% | 22.0422 | 31116.2457
Selected GCR | 0.9 |  | 0.2 | 30% | 1407.24 | 0.3138% | 44.0843 | 62037.1979
Performance | 1219.41 | kWh/kW | 0.3 | 30% | 1400.8 | 0.77% | 66.1265 | 92629.9424
Array Size | 198 | kW | 0.4 | 30% | 1391.58 | 1.423% | 88.1686 | 122693.6753
Annual Production | 241.4432 | MWh | 0.5 | 30% | 1374.37 | 2.642% | 110.2108 | 151470.3669
|  |  | 0.6 | 30% | 1347.43 | 4.551% | 132.2529 | 178201.5467
Zero Energy Array Design |  |  | 0.7 | 30% | 1313.16 | 6.978% | 154.2951 | 202614.1125
Building Source Energy | 4753.3 | GJ | 0.8 | 30% | 1271.63 | 9.92% | 176.3372 | 224235.7009
Site-to-Source Conversion | 3.167 |  | 0.9 | 30% | 1222.29 | 13.42% | 198.3794 | 242477.1252
Needed Site Energy | 416.9126 | MWh | 0.1 | 40% | 1425.64 | 0% | 22.0422 | 31424.1745
Selected Tilt | 30% |  | 0.2 | 40% | 1418.04 | 0.5331% | 44.0843 | 62513.3084
Selected GCR | 0.4 |  | 0.3 | 40% | 1406.95 | 1.311% | 66.1265 | 93036.6201
Oversize By | 10% |  | 0.4 | 40% | 1390.16 | 2.489% | 88.1686 | 122568.4759
Performance | 1391.58 | kWh/kW | 0.5 | 40% | 1362.29 | 4.444% | 110.2108 | 150139.0208
Array Size | 330 | kW | 0.6 | 40% | 1326.86 | 6.929% | 132.2529 | 175481.1042
Annual Production | 459.2214 | MWh | 0.7 | 40% | 1286.68 | 9.747% | 154.2951 | 198528.379
Fits on rooftop? | FALSE |  | 0.8 | 40% | 1243.02 | 12.81% | 176.3372 | 219190.693
|  |  | 0.9 | 40% | 1202.68 | 15.64% | 198.3794 | 238586.9056
Note on F2: Stephen Frank: Generated from PVWatts simulation of a 1 kW array at GCR 0.1-0.9 (by 0.1) and tilt angles 10%-40% (by 10%). - For rooftop system, goal is to maximize production within roof area => higher GCR - For zero energy system, goal is to maximize production overall => lower GCR
Note on H3: Stephen Frank: From PVWatts parametric analysis
Note on C18: Stephen Frank: "Premium" efficiency panels in PVWatts v7
Note on C29: Stephen Frank: Total source energy from EnergyPlus simulation annual summary report
Note on C30: Stephen Frank: Use electricity value from EnergyPlus simulation annual summary report