## Main Xmer
Transformer calculator
Inputs | Estimate |  | Caluclations
Vp | 12470 | V | Ipri | 46.3005 | A
Vs | 480 | V
VA | 1000000 | VA | TR | 25.9792
X/R | 2.38 |  | Zbase_p | 155.5009 | ohm
Zpu | 5.8 | pu | Zbase_s | 0.2304 | ohm
|  |  | theta | 1.173 | rad
no load loss | 1000 |  | rpu | 2.2467 | pu
|  |  | xpu | 5.3472 | pu
[5 empty] | Rp/Rs | 1
|  |  | Rp | 174.6829 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Rs | 0.25882 | ohm
|  |  | Xp | 415.7453 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Xs | 0.61599 | ohm
|  |  | Xmag | 17955.1706
|  |  | Inl | 0.080192 | A
|  |  | IM | 0.69451 | A | 1.5% | Estimated Magnetizing current
|  |  | IR | 0.080192 | A
|  |  | Xm | 17955.1706 | ohm
|  |  | Rc | 155500.9 | ohm

## Main Xmer Efficiency Plot
All calculations approximate
Loading (%) | Nominal Power Output (W) | Current Primary (A) | Winding Loss Primary (W) | Current Secondary (A) | Winding Loss Secondary (W) | Phase Voltage Primary (V) | Phase Voltage Secondary (V) | Core Loss (W) | Total Loss (W) | Efficiency (%)
0% | 0 | 0 | 0 | 0 | 0 | 7199.5579 | 277.1281 | 1000 | 1000 | 0%
2% | 20000 | 0.92598 | 449.3425 | 24.0563 | 449.3425 | 7199.5579 | 277.1281 | 1000 | 1898.6849 | 91.33%
4% | 40000 | 1.852 | 1797.3699 | 48.1125 | 1797.3699 | 7199.5579 | 277.1281 | 1000 | 4594.7397 | 89.7%
6% | 60000 | 2.7779 | 4044.0822 | 72.1688 | 4044.0822 | 7199.5579 | 277.1281 | 1000 | 9088.1643 | 86.85%
8% | 80000 | 3.7039 | 7189.4794 | 96.225 | 7189.4794 | 7199.5579 | 277.1281 | 1000 | 15378.9588 | 83.88%
10% | 100000 | 4.6299 | 11233.5616 | 120.2813 | 11233.5616 | 7199.5579 | 277.1281 | 1000 | 23467.1231 | 80.99%
12% | 120000 | 5.5559 | 16176.3287 | 144.3376 | 16176.3287 | 7199.5579 | 277.1281 | 1000 | 33352.6573 | 78.25%
14% | 140000 | 6.4819 | 22017.7807 | 168.3938 | 22017.7807 | 7199.5579 | 277.1281 | 1000 | 45035.5614 | 75.66%
16% | 160000 | 7.4079 | 28757.9176 | 192.4501 | 28757.9176 | 7199.5579 | 277.1281 | 1000 | 58515.8352 | 73.22%
18% | 180000 | 8.3338 | 36396.7395 | 216.5064 | 36396.7395 | 7199.5579 | 277.1281 | 1000 | 73793.479 | 70.92%
20% | 200000 | 9.2598 | 44934.2463 | 240.5626 | 44934.2463 | 7199.5579 | 277.1281 | 1000 | 90868.4926 | 68.76%
22% | 220000 | 10.1858 | 54370.438 | 264.6189 | 54370.438 | 7199.5579 | 277.1281 | 1000 | 109740.876 | 66.72%
24% | 240000 | 11.1118 | 64705.3147 | 288.6751 | 64705.3147 | 7199.5579 | 277.1281 | 1000 | 130410.6293 | 64.79%
26% | 260000 | 12.0378 | 75938.8762 | 312.7314 | 75938.8762 | 7199.5579 | 277.1281 | 1000 | 152877.7525 | 62.97%
28% | 280000 | 12.9638 | 88071.1227 | 336.7877 | 88071.1227 | 7199.5579 | 277.1281 | 1000 | 177142.2454 | 61.25%
30% | 300000 | 13.8897 | 101102.0541 | 360.8439 | 101102.0541 | 7199.5579 | 277.1281 | 1000 | 203204.1083 | 59.62%
32% | 320000 | 14.8157 | 115031.6705 | 384.9002 | 115031.6705 | 7199.5579 | 277.1281 | 1000 | 231063.341 | 58.07%
34% | 340000 | 15.7417 | 129859.9718 | 408.9564 | 129859.9718 | 7199.5579 | 277.1281 | 1000 | 260719.9435 | 56.6%
36% | 360000 | 16.6677 | 145586.958 | 433.0127 | 145586.958 | 7199.5579 | 277.1281 | 1000 | 292173.9159 | 55.2%
38% | 380000 | 17.5937 | 162212.6291 | 457.069 | 162212.6291 | 7199.5579 | 277.1281 | 1000 | 325425.2582 | 53.87%
40% | 400000 | 18.5197 | 179736.9851 | 481.1252 | 179736.9851 | 7199.5579 | 277.1281 | 1000 | 360473.9703 | 52.6%
42% | 420000 | 19.4456 | 198160.0261 | 505.1815 | 198160.0261 | 7199.5579 | 277.1281 | 1000 | 397320.0523 | 51.39%
44% | 440000 | 20.3716 | 217481.752 | 529.2377 | 217481.752 | 7199.5579 | 277.1281 | 1000 | 435963.5041 | 50.23%
46% | 460000 | 21.2976 | 237702.1629 | 553.294 | 237702.1629 | 7199.5579 | 277.1281 | 1000 | 476404.3257 | 49.12%
48% | 480000 | 22.2236 | 258821.2586 | 577.3503 | 258821.2586 | 7199.5579 | 277.1281 | 1000 | 518642.5172 | 48.07%
50% | 500000 | 23.1496 | 280839.0393 | 601.4065 | 280839.0393 | 7199.5579 | 277.1281 | 1000 | 562678.0786 | 47.05%
52% | 520000 | 24.0756 | 303755.5049 | 625.4628 | 303755.5049 | 7199.5579 | 277.1281 | 1000 | 608511.0098 | 46.08%
54% | 540000 | 25.0015 | 327570.6554 | 649.5191 | 327570.6554 | 7199.5579 | 277.1281 | 1000 | 656141.3109 | 45.15%
56% | 560000 | 25.9275 | 352284.4909 | 673.5753 | 352284.4909 | 7199.5579 | 277.1281 | 1000 | 705568.9818 | 44.25%
58% | 580000 | 26.8535 | 377897.0113 | 697.6316 | 377897.0113 | 7199.5579 | 277.1281 | 1000 | 756794.0226 | 43.39%
60% | 600000 | 27.7795 | 404408.2166 | 721.6878 | 404408.2166 | 7199.5579 | 277.1281 | 1000 | 809816.4332 | 42.56%
62% | 620000 | 28.7055 | 431818.1068 | 745.7441 | 431818.1068 | 7199.5579 | 277.1281 | 1000 | 864636.2136 | 41.76%
64% | 640000 | 29.6314 | 460126.682 | 769.8004 | 460126.682 | 7199.5579 | 277.1281 | 1000 | 921253.364 | 40.99%
66% | 660000 | 30.5574 | 489333.9421 | 793.8566 | 489333.9421 | 7199.5579 | 277.1281 | 1000 | 979667.8841 | 40.25%
68% | 680000 | 31.4834 | 519439.8871 | 817.9129 | 519439.8871 | 7199.5579 | 277.1281 | 1000 | 1039879.7742 | 39.54%
70% | 700000 | 32.4094 | 550444.517 | 841.9691 | 550444.517 | 7199.5579 | 277.1281 | 1000 | 1101889.034 | 38.85%
72% | 720000 | 33.3354 | 582347.8319 | 866.0254 | 582347.8319 | 7199.5579 | 277.1281 | 1000 | 1165695.6638 | 38.18%
74% | 740000 | 34.2614 | 615149.8317 | 890.0817 | 615149.8317 | 7199.5579 | 277.1281 | 1000 | 1231299.6633 | 37.54%
76% | 760000 | 35.1873 | 648850.5164 | 914.1379 | 648850.5164 | 7199.5579 | 277.1281 | 1000 | 1298701.0328 | 36.92%
78% | 780000 | 36.1133 | 683449.886 | 938.1942 | 683449.886 | 7199.5579 | 277.1281 | 1000 | 1367899.7721 | 36.31%
80% | 800000 | 37.0393 | 718947.9406 | 962.2504 | 718947.9406 | 7199.5579 | 277.1281 | 1000 | 1438895.8812 | 35.73%
82% | 820000 | 37.9653 | 755344.6801 | 986.3067 | 755344.6801 | 7199.5579 | 277.1281 | 1000 | 1511689.3602 | 35.17%
84% | 840000 | 38.8913 | 792640.1045 | 1010.363 | 792640.1045 | 7199.5579 | 277.1281 | 1000 | 1586280.209 | 34.62%
86% | 860000 | 39.8173 | 830834.2139 | 1034.4192 | 830834.2139 | 7199.5579 | 277.1281 | 1000 | 1662668.4277 | 34.09%
88% | 880000 | 40.7432 | 869927.0081 | 1058.4755 | 869927.0081 | 7199.5579 | 277.1281 | 1000 | 1740854.0162 | 33.58%
90% | 900000 | 41.6692 | 909918.4873 | 1082.5318 | 909918.4873 | 7199.5579 | 277.1281 | 1000 | 1820836.9746 | 33.08%
92% | 920000 | 42.5952 | 950808.6514 | 1106.588 | 950808.6514 | 7199.5579 | 277.1281 | 1000 | 1902617.3029 | 32.59%
94% | 940000 | 43.5212 | 992597.5005 | 1130.6443 | 992597.5005 | 7199.5579 | 277.1281 | 1000 | 1986195.001 | 32.12%
96% | 960000 | 44.4472 | 1035285.0345 | 1154.7005 | 1035285.0345 | 7199.5579 | 277.1281 | 1000 | 2071570.0689 | 31.67%
98% | 980000 | 45.3732 | 1078871.2534 | 1178.7568 | 1078871.2534 | 7199.5579 | 277.1281 | 1000 | 2158742.5067 | 31.22%
100% | 1000000 | 46.2991 | 1123356.1572 | 1202.8131 | 1123356.1572 | 7199.5579 | 277.1281 | 1000 | 2247712.3144 | 30.79%

## Main Xmer (2)
Transformer calculator
Inputs | Estimate |  | Caluclations
Vp | 12470 | V | Ipri | 46.2991 | A
Vs | 480 | V
VA | 1000000 | VA | TR | 25.9792
X/R | 7.5 |  | Zbase_p | 155.5009 | ohm
Zpu | 5.75% | pu | Zbase_s | 0.2304 | ohm
|  |  | theta | 1.4382 | rad
no load loss | 900 |  | rpu | 0.0075994 | pu
|  |  | xpu | 0.056996 | pu |  | 7.5 | X/R check
[5 empty] | Rp/Rs | 1
|  |  | Rp | 0.59086 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Rs | 0.00087545 | ohm
|  |  | Xp | 4.4314 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Xs | 0.0065659 | ohm
|  |  | Xmag | 17955.6973
|  |  | Inl | 0.072173 | A
|  |  | IM | 0.69449 | A | 1.5% | Estimated Magnetizing current
|  |  | IR | 0.072173 | A
|  |  | Xm | 17955.6973 | ohm
|  |  | Rc | 172778.7778 | ohm
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Zpu was not specified in percent. I fixed it to be percent.
Note on B9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where is this assumption from?
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This adjusted rpu and xpu
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which in turn adjusted these

## Main Xmer Efficiency Plot (2)
All calculations approximate
Loading (%) | Nominal Power Output (W) | Current Primary (A) | Winding Loss Primary (W) | Current Secondary (A) | Winding Loss Secondary (W) | Phase Voltage Primary (V) | Phase Voltage Secondary (V) | Core Loss (W) | Total Loss (W) | Efficiency (%)
0% | 0 | 0 | 0 | 0 | 0 | 7199.5579 | 277.1281 | 900 | 900 | 0%
2% | 20000 | 0.92598 | 1.5199 | 24.0563 | 1.5199 | 7199.5579 | 277.1281 | 900 | 903.0398 | 95.68%
4% | 40000 | 1.852 | 6.0795 | 48.1125 | 6.0795 | 7199.5579 | 277.1281 | 900 | 912.1591 | 97.77%
6% | 60000 | 2.7779 | 13.6789 | 72.1688 | 13.6789 | 7199.5579 | 277.1281 | 900 | 927.3579 | 98.48%
8% | 80000 | 3.7039 | 24.3181 | 96.225 | 24.3181 | 7199.5579 | 277.1281 | 900 | 948.6362 | 98.83%
10% | 100000 | 4.6299 | 37.9971 | 120.2813 | 37.9971 | 7199.5579 | 277.1281 | 900 | 975.9941 | 99.03%
12% | 120000 | 5.5559 | 54.7158 | 144.3376 | 54.7158 | 7199.5579 | 277.1281 | 900 | 1009.4316 | 99.17%
14% | 140000 | 6.4819 | 74.4743 | 168.3938 | 74.4743 | 7199.5579 | 277.1281 | 900 | 1048.9485 | 99.26%
16% | 160000 | 7.4079 | 97.2725 | 192.4501 | 97.2725 | 7199.5579 | 277.1281 | 900 | 1094.545 | 99.32%
18% | 180000 | 8.3338 | 123.1105 | 216.5064 | 123.1105 | 7199.5579 | 277.1281 | 900 | 1146.221 | 99.37%
20% | 200000 | 9.2598 | 151.9883 | 240.5626 | 151.9883 | 7199.5579 | 277.1281 | 900 | 1203.9766 | 99.4%
22% | 220000 | 10.1858 | 183.9058 | 264.6189 | 183.9058 | 7199.5579 | 277.1281 | 900 | 1267.8116 | 99.43%
24% | 240000 | 11.1118 | 218.8631 | 288.6751 | 218.8631 | 7199.5579 | 277.1281 | 900 | 1337.7262 | 99.45%
26% | 260000 | 12.0378 | 256.8602 | 312.7314 | 256.8602 | 7199.5579 | 277.1281 | 900 | 1413.7204 | 99.46%
28% | 280000 | 12.9638 | 297.897 | 336.7877 | 297.897 | 7199.5579 | 277.1281 | 900 | 1495.7941 | 99.47%
30% | 300000 | 13.8897 | 341.9736 | 360.8439 | 341.9736 | 7199.5579 | 277.1281 | 900 | 1583.9473 | 99.47%
32% | 320000 | 14.8157 | 389.09 | 384.9002 | 389.09 | 7199.5579 | 277.1281 | 900 | 1678.18 | 99.48%
34% | 340000 | 15.7417 | 439.2461 | 408.9564 | 439.2461 | 7199.5579 | 277.1281 | 900 | 1778.4922 | 99.48%
36% | 360000 | 16.6677 | 492.442 | 433.0127 | 492.442 | 7199.5579 | 277.1281 | 900 | 1884.884 | 99.48%
38% | 380000 | 17.5937 | 548.6777 | 457.069 | 548.6777 | 7199.5579 | 277.1281 | 900 | 1997.3554 | 99.48%
40% | 400000 | 18.5197 | 607.9531 | 481.1252 | 607.9531 | 7199.5579 | 277.1281 | 900 | 2115.9062 | 99.47%
42% | 420000 | 19.4456 | 670.2683 | 505.1815 | 670.2683 | 7199.5579 | 277.1281 | 900 | 2240.5366 | 99.47%
44% | 440000 | 20.3716 | 735.6233 | 529.2377 | 735.6233 | 7199.5579 | 277.1281 | 900 | 2371.2465 | 99.46%
46% | 460000 | 21.2976 | 804.018 | 553.294 | 804.018 | 7199.5579 | 277.1281 | 900 | 2508.036 | 99.46%
48% | 480000 | 22.2236 | 875.4525 | 577.3503 | 875.4525 | 7199.5579 | 277.1281 | 900 | 2650.905 | 99.45%
50% | 500000 | 23.1496 | 949.9267 | 601.4065 | 949.9267 | 7199.5579 | 277.1281 | 900 | 2799.8535 | 99.44%
52% | 520000 | 24.0756 | 1027.4408 | 625.4628 | 1027.4408 | 7199.5579 | 277.1281 | 900 | 2954.8815 | 99.43%
54% | 540000 | 25.0015 | 1107.9945 | 649.5191 | 1107.9945 | 7199.5579 | 277.1281 | 900 | 3115.9891 | 99.43%
56% | 560000 | 25.9275 | 1191.5881 | 673.5753 | 1191.5881 | 7199.5579 | 277.1281 | 900 | 3283.1762 | 99.42%
58% | 580000 | 26.8535 | 1278.2214 | 697.6316 | 1278.2214 | 7199.5579 | 277.1281 | 900 | 3456.4428 | 99.41%
60% | 600000 | 27.7795 | 1367.8945 | 721.6878 | 1367.8945 | 7199.5579 | 277.1281 | 900 | 3635.789 | 99.4%
62% | 620000 | 28.7055 | 1460.6074 | 745.7441 | 1460.6074 | 7199.5579 | 277.1281 | 900 | 3821.2147 | 99.39%
64% | 640000 | 29.6314 | 1556.36 | 769.8004 | 1556.36 | 7199.5579 | 277.1281 | 900 | 4012.7199 | 99.38%
66% | 660000 | 30.5574 | 1655.1523 | 793.8566 | 1655.1523 | 7199.5579 | 277.1281 | 900 | 4210.3047 | 99.37%
68% | 680000 | 31.4834 | 1756.9845 | 817.9129 | 1756.9845 | 7199.5579 | 277.1281 | 900 | 4413.969 | 99.36%
70% | 700000 | 32.4094 | 1861.8564 | 841.9691 | 1861.8564 | 7199.5579 | 277.1281 | 900 | 4623.7128 | 99.34%
72% | 720000 | 33.3354 | 1969.7681 | 866.0254 | 1969.7681 | 7199.5579 | 277.1281 | 900 | 4839.5362 | 99.33%
74% | 740000 | 34.2614 | 2080.7195 | 890.0817 | 2080.7195 | 7199.5579 | 277.1281 | 900 | 5061.4391 | 99.32%
76% | 760000 | 35.1873 | 2194.7107 | 914.1379 | 2194.7107 | 7199.5579 | 277.1281 | 900 | 5289.4215 | 99.31%
78% | 780000 | 36.1133 | 2311.7417 | 938.1942 | 2311.7417 | 7199.5579 | 277.1281 | 900 | 5523.4834 | 99.3%
80% | 800000 | 37.0393 | 2431.8124 | 962.2504 | 2431.8124 | 7199.5579 | 277.1281 | 900 | 5763.6249 | 99.28%
82% | 820000 | 37.9653 | 2554.923 | 986.3067 | 2554.923 | 7199.5579 | 277.1281 | 900 | 6009.8459 | 99.27%
84% | 840000 | 38.8913 | 2681.0732 | 1010.363 | 2681.0732 | 7199.5579 | 277.1281 | 900 | 6262.1465 | 99.26%
86% | 860000 | 39.8173 | 2810.2633 | 1034.4192 | 2810.2633 | 7199.5579 | 277.1281 | 900 | 6520.5265 | 99.25%
88% | 880000 | 40.7432 | 2942.4931 | 1058.4755 | 2942.4931 | 7199.5579 | 277.1281 | 900 | 6784.9861 | 99.23%
90% | 900000 | 41.6692 | 3077.7626 | 1082.5318 | 3077.7626 | 7199.5579 | 277.1281 | 900 | 7055.5253 | 99.22%
92% | 920000 | 42.5952 | 3216.072 | 1106.588 | 3216.072 | 7199.5579 | 277.1281 | 900 | 7332.1439 | 99.21%
94% | 940000 | 43.5212 | 3357.4211 | 1130.6443 | 3357.4211 | 7199.5579 | 277.1281 | 900 | 7614.8421 | 99.2%
96% | 960000 | 44.4472 | 3501.8099 | 1154.7005 | 3501.8099 | 7199.5579 | 277.1281 | 900 | 7903.6199 | 99.18%
98% | 980000 | 45.3732 | 3649.2386 | 1178.7568 | 3649.2386 | 7199.5579 | 277.1281 | 900 | 8198.4771 | 99.17%
100% | 1000000 | 46.2991 | 3799.707 | 1202.8131 | 3799.707 | 7199.5579 | 277.1281 | 900 | 8499.4139 | 99.16%

## MEL Xmer
Transformer calculator
Inputs | Estimate |  | Caluclations
Vp | 277 | V | Ipri | 234.4903 | A
Vs | 208 | V
VA | 112500 | VA | TR | 1.3317
X/R | 1.51 |  | Zbase_p | 0.68204 | ohm
Zpu | 6.1 | pu | Zbase_s | 0.38457 | ohm
|  |  | theta | 0.98586 | rad
no load loss | 168.75 |  | rpu | 3.3681 | pu
|  |  | xpu | 5.0858 | pu
|  |  | Rp/Rs | 1
|  |  | Rp | 1.1486 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Rs | 0.64764 | ohm
|  |  | Xp | 1.7344 | ohm | 2 | Ratio of primary and secondary winding
|  |  | Xs | 0.97793 | ohm
|  |  | Inl | 0.60921 | A
|  |  | IM | 5.8623 | A | 2.5% | Estimated Magnetizing current
|  |  | IR | 0.60921 | A
|  |  | Xm | 47.2514 | ohm
|  |  | Rc | 454.6904 | ohm

## Xmer Calc_Main
Inputs |  |  |  | Per-Unit Bases
DOE Efficiency | 99.43% |  |  | S_Base | 1000000 | VA
Efficiency Buffer | 0.01% |  |  | Vp_Base | 12470 | V_LL
Efficiency | 99.44% |  |  | Vs_Base | 480 | V_LL
At Loading | 50% |  |  | Ip_Base | 46.2991 | A
Primary Voltage | 12470 | V_LL |  | Is_Base | 1202.8131 | A
Secondary Voltage | 480 | V_LL |  | Zp_Base | 155.5009 | Ohm
Power Rating | 1000000 | VA |  | Zs_Base | 0.2304 | Ohm
Z_Series | 0.058 | pu
Magnetizing current | 0.015 | pu
Resistance ratio Rp/Rs | 1
Reactance ratio Xp/Xs | 1
Calculated Values (Per-Unit)
Current at peak efficiency | 0.5 | pu
Series resistance R_Se | 0.0056315 | pu | See word doc |  |  |  | 0.0028158
Core loss resistance R_C | 710.2857 | pu | See word doc
Series reactance X_Se | 0.057726 | pu | Z^2 = X^2 + R^2 |  |  |  | 0.028863
Magnetizing reactance X_M | 66.6667 | pu | Neglecting core loss component of no-load current
Calculated Values (Volt-Ampere)
Primary winding resistance Rp | 0.43785 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding resistance Rs | 0.00064875 | Ohm | Wye secondary
Primary winding reactance Xp | 4.4882 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding reactance Xs | 0.00665 | Ohm | Wye secondary
Core loss resistance R_C | 110450.0678 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)
Magnetizing reactance X_M | 10366.7267 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)

## Xmer Calc Eff Plot
All calculations approximate
Loading (%) | Nominal Power Output (W) | Current Primary (A) | Winding Loss Primary (W) | Current Secondary (A) | Winding Loss Secondary (W) | Phase Voltage Primary (V) | Phase Voltage Secondary (V) | Core Loss (W) | Total Loss (W) | Efficiency (%)
0% | 0 | 0 | 0 | 0 | 0 | 7199.5579 | 277.1281 | 1407.8842 | 1407.8842 | 0%
2% | 20000 | 0.92598 | 1.1263 | 24.0563 | 1.1263 | 7199.5579 | 277.1281 | 1407.8842 | 1410.1368 | 93.41%
4% | 40000 | 1.852 | 4.5052 | 48.1125 | 4.5052 | 7199.5579 | 277.1281 | 1407.8842 | 1416.8946 | 96.58%
6% | 60000 | 2.7779 | 10.1368 | 72.1688 | 10.1368 | 7199.5579 | 277.1281 | 1407.8842 | 1428.1577 | 97.68%
8% | 80000 | 3.7039 | 18.0209 | 96.225 | 18.0209 | 7199.5579 | 277.1281 | 1407.8842 | 1443.926 | 98.23%
10% | 100000 | 4.6299 | 28.1577 | 120.2813 | 28.1577 | 7199.5579 | 277.1281 | 1407.8842 | 1464.1995 | 98.56%
12% | 120000 | 5.5559 | 40.5471 | 144.3376 | 40.5471 | 7199.5579 | 277.1281 | 1407.8842 | 1488.9783 | 98.77%
14% | 140000 | 6.4819 | 55.1891 | 168.3938 | 55.1891 | 7199.5579 | 277.1281 | 1407.8842 | 1518.2623 | 98.93%
16% | 160000 | 7.4079 | 72.0837 | 192.4501 | 72.0837 | 7199.5579 | 277.1281 | 1407.8842 | 1552.0515 | 99.04%
18% | 180000 | 8.3338 | 91.2309 | 216.5064 | 91.2309 | 7199.5579 | 277.1281 | 1407.8842 | 1590.3459 | 99.12%
20% | 200000 | 9.2598 | 112.6307 | 240.5626 | 112.6307 | 7199.5579 | 277.1281 | 1407.8842 | 1633.1456 | 99.19%
22% | 220000 | 10.1858 | 136.2832 | 264.6189 | 136.2832 | 7199.5579 | 277.1281 | 1407.8842 | 1680.4505 | 99.24%
24% | 240000 | 11.1118 | 162.1883 | 288.6751 | 162.1883 | 7199.5579 | 277.1281 | 1407.8842 | 1732.2607 | 99.28%
26% | 260000 | 12.0378 | 190.3459 | 312.7314 | 190.3459 | 7199.5579 | 277.1281 | 1407.8842 | 1788.576 | 99.32%
28% | 280000 | 12.9638 | 220.7562 | 336.7877 | 220.7562 | 7199.5579 | 277.1281 | 1407.8842 | 1849.3966 | 99.34%
30% | 300000 | 13.8897 | 253.4191 | 360.8439 | 253.4191 | 7199.5579 | 277.1281 | 1407.8842 | 1914.7224 | 99.37%
32% | 320000 | 14.8157 | 288.3347 | 384.9002 | 288.3347 | 7199.5579 | 277.1281 | 1407.8842 | 1984.5535 | 99.38%
34% | 340000 | 15.7417 | 325.5028 | 408.9564 | 325.5028 | 7199.5579 | 277.1281 | 1407.8842 | 2058.8898 | 99.4%
36% | 360000 | 16.6677 | 364.9236 | 433.0127 | 364.9236 | 7199.5579 | 277.1281 | 1407.8842 | 2137.7313 | 99.41%
38% | 380000 | 17.5937 | 406.5969 | 457.069 | 406.5969 | 7199.5579 | 277.1281 | 1407.8842 | 2221.078 | 99.42%
40% | 400000 | 18.5197 | 450.5229 | 481.1252 | 450.5229 | 7199.5579 | 277.1281 | 1407.8842 | 2308.93 | 99.43%
42% | 420000 | 19.4456 | 496.7015 | 505.1815 | 496.7015 | 7199.5579 | 277.1281 | 1407.8842 | 2401.2872 | 99.43%
44% | 440000 | 20.3716 | 545.1327 | 529.2377 | 545.1327 | 7199.5579 | 277.1281 | 1407.8842 | 2498.1496 | 99.44%
46% | 460000 | 21.2976 | 595.8166 | 553.294 | 595.8166 | 7199.5579 | 277.1281 | 1407.8842 | 2599.5173 | 99.44%
48% | 480000 | 22.2236 | 648.753 | 577.3503 | 648.753 | 7199.5579 | 277.1281 | 1407.8842 | 2705.3902 | 99.44%
50% | 500000 | 23.1496 | 703.9421 | 601.4065 | 703.9421 | 7199.5579 | 277.1281 | 1407.8842 | 2815.7683 | 99.44%
52% | 520000 | 24.0756 | 761.3837 | 625.4628 | 761.3837 | 7199.5579 | 277.1281 | 1407.8842 | 2930.6516 | 99.44%
54% | 540000 | 25.0015 | 821.078 | 649.5191 | 821.078 | 7199.5579 | 277.1281 | 1407.8842 | 3050.0402 | 99.44%
56% | 560000 | 25.9275 | 883.0249 | 673.5753 | 883.0249 | 7199.5579 | 277.1281 | 1407.8842 | 3173.934 | 99.44%
58% | 580000 | 26.8535 | 947.2245 | 697.6316 | 947.2245 | 7199.5579 | 277.1281 | 1407.8842 | 3302.3331 | 99.43%
60% | 600000 | 27.7795 | 1013.6766 | 721.6878 | 1013.6766 | 7199.5579 | 277.1281 | 1407.8842 | 3435.2373 | 99.43%
62% | 620000 | 28.7055 | 1082.3813 | 745.7441 | 1082.3813 | 7199.5579 | 277.1281 | 1407.8842 | 3572.6468 | 99.43%
64% | 640000 | 29.6314 | 1153.3387 | 769.8004 | 1153.3387 | 7199.5579 | 277.1281 | 1407.8842 | 3714.5615 | 99.42%
66% | 660000 | 30.5574 | 1226.5487 | 793.8566 | 1226.5487 | 7199.5579 | 277.1281 | 1407.8842 | 3860.9815 | 99.42%
68% | 680000 | 31.4834 | 1302.0113 | 817.9129 | 1302.0113 | 7199.5579 | 277.1281 | 1407.8842 | 4011.9067 | 99.41%
70% | 700000 | 32.4094 | 1379.7265 | 841.9691 | 1379.7265 | 7199.5579 | 277.1281 | 1407.8842 | 4167.3371 | 99.41%
72% | 720000 | 33.3354 | 1459.6943 | 866.0254 | 1459.6943 | 7199.5579 | 277.1281 | 1407.8842 | 4327.2727 | 99.4%
74% | 740000 | 34.2614 | 1541.9147 | 890.0817 | 1541.9147 | 7199.5579 | 277.1281 | 1407.8842 | 4491.7136 | 99.4%
76% | 760000 | 35.1873 | 1626.3878 | 914.1379 | 1626.3878 | 7199.5579 | 277.1281 | 1407.8842 | 4660.6597 | 99.39%
78% | 780000 | 36.1133 | 1713.1134 | 938.1942 | 1713.1134 | 7199.5579 | 277.1281 | 1407.8842 | 4834.111 | 99.38%
80% | 800000 | 37.0393 | 1802.0917 | 962.2504 | 1802.0917 | 7199.5579 | 277.1281 | 1407.8842 | 5012.0676 | 99.38%
82% | 820000 | 37.9653 | 1893.3226 | 986.3067 | 1893.3226 | 7199.5579 | 277.1281 | 1407.8842 | 5194.5294 | 99.37%
84% | 840000 | 38.8913 | 1986.8061 | 1010.363 | 1986.8061 | 7199.5579 | 277.1281 | 1407.8842 | 5381.4964 | 99.36%
86% | 860000 | 39.8173 | 2082.5422 | 1034.4192 | 2082.5422 | 7199.5579 | 277.1281 | 1407.8842 | 5572.9686 | 99.36%
88% | 880000 | 40.7432 | 2180.531 | 1058.4755 | 2180.531 | 7199.5579 | 277.1281 | 1407.8842 | 5768.9461 | 99.35%
90% | 900000 | 41.6692 | 2280.7723 | 1082.5318 | 2280.7723 | 7199.5579 | 277.1281 | 1407.8842 | 5969.4288 | 99.34%
92% | 920000 | 42.5952 | 2383.2663 | 1106.588 | 2383.2663 | 7199.5579 | 277.1281 | 1407.8842 | 6174.4167 | 99.33%
94% | 940000 | 43.5212 | 2488.0129 | 1130.6443 | 2488.0129 | 7199.5579 | 277.1281 | 1407.8842 | 6383.9099 | 99.33%
96% | 960000 | 44.4472 | 2595.0121 | 1154.7005 | 2595.0121 | 7199.5579 | 277.1281 | 1407.8842 | 6597.9083 | 99.32%
98% | 980000 | 45.3732 | 2704.2639 | 1178.7568 | 2704.2639 | 7199.5579 | 277.1281 | 1407.8842 | 6816.4119 | 99.31%
100% | 1000000 | 46.2991 | 2815.7683 | 1202.8131 | 2815.7683 | 7199.5579 | 277.1281 | 1407.8842 | 7039.4208 | 99.3% |  | 7130
[11 empty] | division.u2 | 1007130
[11 empty] | Local Min | 1407.47 at 0
[11 empty] | Local Max | 1.00713e+06 at 110
[11 empty] | Slope | 10115.3
[11 empty] | Time | 110 | s

## Xmer Calc_AC_MEL
Inputs |  |  |  | Per-Unit Bases
DOE Efficiency | 98.74% |  |  | S_Base | 112500 | VA
Efficiency Buffer | 0.02% |  |  | Vp_Base | 480 | V_LL
Efficiency | 98.76% |  |  | Vs_Base | 208 | V_LL
At Loading | 35% |  |  | Ip_Base | 135.3165 | A
Primary Voltage | 480 | V_LL |  | Is_Base | 312.2688 | A
Secondary Voltage | 208 | V_LL |  | Zp_Base | 2.048 | Ohm
Power Rating | 112500 | VA |  | Zs_Base | 0.38457 | Ohm
Z_Series | 0.04 | pu
Magnetizing current | 0.025 | pu
Resistance ratio Rp/Rs | 1
Reactance ratio Xp/Xs | 1
Calculated Values (Per-Unit)
Current at peak efficiency | 0.35 | pu
Series resistance R_Se | 0.017937 | pu | See word doc |  |  |  | 0.0089684
Core loss resistance R_C | 455.1152 | pu | See word doc
Series reactance X_Se | 0.035753 | pu | Z^2 = X^2 + R^2 |  |  |  | 0.017876
Magnetizing reactance X_M | 40 | pu | Neglecting core loss component of no-load current
Calculated Values (Volt-Ampere)
Primary winding resistance Rp | 0.018367 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding resistance Rs | 0.0034489 | Ohm | Wye secondary
Primary winding reactance Xp | 0.036611 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding reactance Xs | 0.0068747 | Ohm | Wye secondary
Core loss resistance R_C | 932.0759 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)
Magnetizing reactance X_M | 81.92 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)

## Xmer Calc Eff_MEL
All calculations approximate
Loading (%) | Nominal Power Output (W) | Current Primary (A) | Winding Loss Primary (W) | Current Secondary (A) | Winding Loss Secondary (W) | Phase Voltage Primary (V) | Phase Voltage Secondary (V) | Core Loss (W) | Total Loss (W) | Efficiency (%)
0% | 0 | 0 | 0 | 0 | 0 | 277.1281 | 120.0889 | 247.1902 | 247.1902 | 0%
2% | 2250 | 2.7063 | 0.40358 | 6.2454 | 0.40358 | 277.1281 | 120.0889 | 247.1902 | 247.9973 | 90.07%
4% | 4500 | 5.4127 | 1.6143 | 12.4908 | 1.6143 | 277.1281 | 120.0889 | 247.1902 | 250.4188 | 94.73%
6% | 6750 | 8.119 | 3.6322 | 18.7361 | 3.6322 | 277.1281 | 120.0889 | 247.1902 | 254.4545 | 96.37%
8% | 9000 | 10.8253 | 6.4572 | 24.9815 | 6.4572 | 277.1281 | 120.0889 | 247.1902 | 260.1046 | 97.19%
10% | 11250 | 13.5316 | 10.0894 | 31.2269 | 10.0894 | 277.1281 | 120.0889 | 247.1902 | 267.3689 | 97.68%
12% | 13500 | 16.238 | 14.5287 | 37.4723 | 14.5287 | 277.1281 | 120.0889 | 247.1902 | 276.2476 | 97.99%
14% | 15750 | 18.9443 | 19.7752 | 43.7176 | 19.7752 | 277.1281 | 120.0889 | 247.1902 | 286.7406 | 98.21%
16% | 18000 | 21.6506 | 25.8288 | 49.963 | 25.8288 | 277.1281 | 120.0889 | 247.1902 | 298.8479 | 98.37%
18% | 20250 | 24.357 | 32.6896 | 56.2084 | 32.6896 | 277.1281 | 120.0889 | 247.1902 | 312.5694 | 98.48%
20% | 22500 | 27.0633 | 40.3576 | 62.4538 | 40.3576 | 277.1281 | 120.0889 | 247.1902 | 327.9053 | 98.56%
22% | 24750 | 29.7696 | 48.8327 | 68.6991 | 48.8327 | 277.1281 | 120.0889 | 247.1902 | 344.8555 | 98.63%
24% | 27000 | 32.476 | 58.1149 | 74.9445 | 58.1149 | 277.1281 | 120.0889 | 247.1902 | 363.42 | 98.67%
26% | 29250 | 35.1823 | 68.2043 | 81.1899 | 68.2043 | 277.1281 | 120.0889 | 247.1902 | 383.5988 | 98.71%
28% | 31500 | 37.8886 | 79.1009 | 87.4353 | 79.1009 | 277.1281 | 120.0889 | 247.1902 | 405.3919 | 98.73%
30% | 33750 | 40.5949 | 90.8045 | 93.6806 | 90.8045 | 277.1281 | 120.0889 | 247.1902 | 428.7993 | 98.75%
32% | 36000 | 43.3013 | 103.3154 | 99.926 | 103.3154 | 277.1281 | 120.0889 | 247.1902 | 453.821 | 98.76%
34% | 38250 | 46.0076 | 116.6334 | 106.1714 | 116.6334 | 277.1281 | 120.0889 | 247.1902 | 480.457 | 98.76%
36% | 40500 | 48.7139 | 130.7585 | 112.4168 | 130.7585 | 277.1281 | 120.0889 | 247.1902 | 508.7073 | 98.76%
38% | 42750 | 51.4203 | 145.6909 | 118.6621 | 145.6909 | 277.1281 | 120.0889 | 247.1902 | 538.5719 | 98.76%
40% | 45000 | 54.1266 | 161.4303 | 124.9075 | 161.4303 | 277.1281 | 120.0889 | 247.1902 | 570.0508 | 98.75%
42% | 47250 | 56.8329 | 177.9769 | 131.1529 | 177.9769 | 277.1281 | 120.0889 | 247.1902 | 603.144 | 98.74%
44% | 49500 | 59.5392 | 195.3307 | 137.3983 | 195.3307 | 277.1281 | 120.0889 | 247.1902 | 637.8515 | 98.73%
46% | 51750 | 62.2456 | 213.4916 | 143.6436 | 213.4916 | 277.1281 | 120.0889 | 247.1902 | 674.1733 | 98.71%
48% | 54000 | 64.9519 | 232.4596 | 149.889 | 232.4596 | 277.1281 | 120.0889 | 247.1902 | 712.1094 | 98.7%
50% | 56250 | 67.6582 | 252.2349 | 156.1344 | 252.2349 | 277.1281 | 120.0889 | 247.1902 | 751.6599 | 98.68%
52% | 58500 | 70.3646 | 272.8172 | 162.3798 | 272.8172 | 277.1281 | 120.0889 | 247.1902 | 792.8246 | 98.66%
54% | 60750 | 73.0709 | 294.2067 | 168.6251 | 294.2067 | 277.1281 | 120.0889 | 247.1902 | 835.6036 | 98.64%
56% | 63000 | 75.7772 | 316.4034 | 174.8705 | 316.4034 | 277.1281 | 120.0889 | 247.1902 | 879.997 | 98.62%
58% | 65250 | 78.4836 | 339.4072 | 181.1159 | 339.4072 | 277.1281 | 120.0889 | 247.1902 | 926.0046 | 98.6%
60% | 67500 | 81.1899 | 363.2182 | 187.3613 | 363.2182 | 277.1281 | 120.0889 | 247.1902 | 973.6265 | 98.58%
62% | 69750 | 83.8962 | 387.8363 | 193.6066 | 387.8363 | 277.1281 | 120.0889 | 247.1902 | 1022.8628 | 98.55%
64% | 72000 | 86.6025 | 413.2616 | 199.852 | 413.2616 | 277.1281 | 120.0889 | 247.1902 | 1073.7133 | 98.53%
66% | 74250 | 89.3089 | 439.494 | 206.0974 | 439.494 | 277.1281 | 120.0889 | 247.1902 | 1126.1782 | 98.51%
68% | 76500 | 92.0152 | 466.5336 | 212.3428 | 466.5336 | 277.1281 | 120.0889 | 247.1902 | 1180.2573 | 98.48%
70% | 78750 | 94.7215 | 494.3803 | 218.5881 | 494.3803 | 277.1281 | 120.0889 | 247.1902 | 1235.9508 | 98.45%
72% | 81000 | 97.4279 | 523.0342 | 224.8335 | 523.0342 | 277.1281 | 120.0889 | 247.1902 | 1293.2585 | 98.43%
74% | 83250 | 100.1342 | 552.4952 | 231.0789 | 552.4952 | 277.1281 | 120.0889 | 247.1902 | 1352.1806 | 98.4%
76% | 85500 | 102.8405 | 582.7634 | 237.3243 | 582.7634 | 277.1281 | 120.0889 | 247.1902 | 1412.717 | 98.37%
78% | 87750 | 105.5468 | 613.8387 | 243.5696 | 613.8387 | 277.1281 | 120.0889 | 247.1902 | 1474.8676 | 98.35%
80% | 90000 | 108.2532 | 645.7212 | 249.815 | 645.7212 | 277.1281 | 120.0889 | 247.1902 | 1538.6326 | 98.32%
82% | 92250 | 110.9595 | 678.4109 | 256.0604 | 678.4109 | 277.1281 | 120.0889 | 247.1902 | 1604.0119 | 98.29%
84% | 94500 | 113.6658 | 711.9077 | 262.3058 | 711.9077 | 277.1281 | 120.0889 | 247.1902 | 1671.0055 | 98.26%
86% | 96750 | 116.3722 | 746.2116 | 268.5511 | 746.2116 | 277.1281 | 120.0889 | 247.1902 | 1739.6133 | 98.23%
88% | 99000 | 119.0785 | 781.3227 | 274.7965 | 781.3227 | 277.1281 | 120.0889 | 247.1902 | 1809.8355 | 98.2%
90% | 101250 | 121.7848 | 817.2409 | 281.0419 | 817.2409 | 277.1281 | 120.0889 | 247.1902 | 1881.672 | 98.18%
92% | 103500 | 124.4912 | 853.9663 | 287.2873 | 853.9663 | 277.1281 | 120.0889 | 247.1902 | 1955.1228 | 98.15%
94% | 105750 | 127.1975 | 891.4989 | 293.5326 | 891.4989 | 277.1281 | 120.0889 | 247.1902 | 2030.1879 | 98.12%
96% | 108000 | 129.9038 | 929.8386 | 299.778 | 929.8386 | 277.1281 | 120.0889 | 247.1902 | 2106.8673 | 98.09%
98% | 110250 | 132.6101 | 968.9854 | 306.0234 | 968.9854 | 277.1281 | 120.0889 | 247.1902 | 2185.161 | 98.06%
100% | 112500 | 135.3165 | 1008.9394 | 312.2688 | 1008.9394 | 277.1281 | 120.0889 | 247.1902 | 2265.069 | 98.03% |  | 2322
[11 empty] | division.u2 | 114822
[11 empty] | Local Min | 247.603 at 0
[11 empty] | Local Max | 114847 at 110
[11 empty] | Slope | 1167.82
[11 empty] | Time | 109.979 | s

## Xmer Calc_AC_MEL_red
Inputs |  |  |  | Per-Unit Bases
DOE Efficiency | 98.6% |  |  | S_Base | 75000 | VA
Efficiency Buffer | 0.02% |  |  | Vp_Base | 480 | V_LL
Efficiency | 98.62% |  |  | Vs_Base | 208 | V_LL
At Loading | 35% |  |  | Ip_Base | 90.211 | A
Primary Voltage | 480 | V_LL |  | Is_Base | 208.1792 | A
Secondary Voltage | 208 | V_LL |  | Zp_Base | 3.072 | Ohm
Power Rating | 75000 | VA |  | Zs_Base | 0.57685 | Ohm
Z_Series | 0.035 | pu
Magnetizing current | 0.03 | pu
Resistance ratio Rp/Rs | 1
Reactance ratio Xp/Xs | 1
Calculated Values (Per-Unit)
Current at peak efficiency | 0.35 | pu
Series resistance R_Se | 0.01999 | pu | See word doc |  |  |  | 0.0099951
Core loss resistance R_C | 408.3644 | pu | See word doc
Series reactance X_Se | 0.02873 | pu | Z^2 = X^2 + R^2 |  |  |  | 0.014365
Magnetizing reactance X_M | 33.3333 | pu | Neglecting core loss component of no-load current
Calculated Values (Volt-Ampere)
Primary winding resistance Rp | 0.030705 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding resistance Rs | 0.0057657 | Ohm | Wye secondary
Primary winding reactance Xp | 0.044129 | Ohm | Delta primary: multiply by 3 in Modelica
Secondary winding reactance Xs | 0.0082864 | Ohm | Wye secondary
Core loss resistance R_C | 1254.4954 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)
Magnetizing reactance X_M | 102.4 | Ohm | Modeled on transformer primary side (line-to-line: multiply by 3 in Modelica)

## Transformer Calculator (2)
Inputs |  |  |  | Per-Unit Bases |  |  | Transformer calculator
Efficiency | 99.6% |  |  | S_Base | 1000000 | VA | Inputs | Estimate |  |  | Caluclations
At Loading | 50% |  |  | Vp_Base | 12470 | V_LL | Vp | 12470 | V |  | Ipri | 46.2991 | A
Primary Voltage | 12470 | V_LL |  | Vs_Base | 480 | V_LL | Vs | 480 | V |  | Isec | 1202.8131 | A
Secondary Voltage | 480 | V_LL |  | Ip_Base | 46.2991 | A | VA | 1000000 | VA |  | TR | 25.9792
Power Rating | 1000000 | VA |  | Is_Base | 1202.8131 | A | X/R | 6 |  |  | Zbase_p | 155.5009 | ohm
Z_Series | 0.058 | pu |  | Zp_Base | 155.5009 | Ohm | Zpu | 5.8% | pu |  | Zbase_s | 0.2304 | ohm
Magnetizing current | 0.015 | pu |  | Zs_Base | 0.2304 | Ohm |  |  |  |  | theta | 1.4056 | rad
Resistance ratio Rp/Rs | 1 | [5 empty] | no load loss | 700 |  |  | rpu | 0.0095351 | pu
Reactance ratio Xp/Xs | 1 | [9 empty] | xpu | 0.057211 | pu |  | 6 | X/R check
Calculated Values (Per-Unit) | [9 empty] | i2r |  |  | Rp/Rs | 1
Current at peak efficiency | 0.5 | pu | [7 empty] | 1589.1902 | Rp | 0.74136 | ohm | 0.5 | Ratio of primary and secondary winding
Series resistance R_Se | 0.0040161 | pu | See word doc | [6 empty] | 1589.1902 | Rs | 0.0010984 | ohm
Core loss resistance R_C | 996 | pu | See word doc | [7 empty] | Xp | 4.4482 | ohm | 2 | Ratio of primary and secondary winding
Series reactance X_Se | 0.057861 | pu | Z^2 = X^2 + R^2 | [7 empty] | Xs | 0.0065907 | ohm
Magnetizing reactance X_M | 66.6667 | pu | Neglecting core loss component of no-load current
[11 empty] | Xmag | 17955.6973
Calculated Values (Volt-Ampere) | [10 empty] | Inl | 0.056135 | A
Primary winding resistance Rp | 0.31225 | Ohm | [8 empty] | IM | 0.69449 | A | 1.5% | Estimated Magnetizing current
Secondary winding resistance Rs | 0.00046265 | Ohm | [8 empty] | IR | 0.056135 | A
Primary winding reactance Xp | 4.4987 | Ohm
Secondary winding reactance Xs | 0.0066656 | Ohm | [8 empty] | Xm | 17955.6973 | ohm
Core loss resistance R_C | 154878.8964 | Ohm | Modeled on transformer primary side | [7 empty] | Rc | 222144.1429 | ohm
Magnetizing reactance X_M | 10366.7267 | Ohm | Modeled on transformer primary side
Note on J7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Zpu was not specified in percent. I fixed it to be percent.
Note on J9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where is this assumption from?
Note on N9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This adjusted rpu and xpu
Note on N13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which in turn adjusted these