## Floor 1
Versioning Information
Building Category | Commercial
Building Type | Medium Office
Code/Year | ASHRAE 90.1-2019
Location | All
Floor Characteristics
Floor Number: | 1
Floor Area: | 17866.6667 | ft²
| 1659.8676 | m²
Total Receptacles: | 405
Effective Load: | 13401.9994 | W
Power Density: | 8.0741 | W/m²
Connected Plug Load
Device Type | Density (Qty. per 1000 ft²) | Number of Devices | Design Maximum | Rated Unit Power (Wrated) | Demand Factor (Wpeak/Wrated) | Connected Load (Wrated) | Effective Load (W) | Notes
Desktop computers | 0 | 0 | - | 1046 | 0.115 | 0 | 0 | Assume all desktop computers converted to laptop computers.
Laptop computers | 2.81 | 50 | 68 | 57 | 0.322 | 2850 | 917.7
Monitors | 1.87 | 33 | 68 | 46 | 0.558 | 1518 | 847.044
TVs / displays | 0.26 | 5 | 25 | 127 | 0.558 | 635 | 354.33
Copiers | 0 | 0 | - | 648 | 0.271 | 0 | 0 | NEMs density < 1 per 100,000 ft². Assume none (MFDs only).
Printers | 0.52 | 9 | - | 875 | 0.271 | 7875 | 2134.125
Multi-Function Devices | 0.17 | 3 | - | 684 | 0.271 | 2052 | 556.092
IT Equipment | 3.078 | 55 | - | 160 | 0.225 | 8800 | 1980 | NEMs density is very high; assume fewer, larger devices
Other / Empty |  | 250 | 244 |  |  |  | 6612.7084
Total |  | 405 |  |  |  | 23730 | 13401.9994
Note on C12: Per electrical circuit design
Note on C13: Effective connected load derived from EnergyPlus input description file (IDF); excludes elevators.
Note on C17: See Plug Load Characteristics spreadsheet
Note on E17: Maximum number of devices based on design occupancy of detailed furniture layout by PNNL team. For reference only.
Note on F17: See Plug Load Characteristics spreadsheet
Note on G17: See Plug Load Characteristics spreadsheet
Note on H17: Total connected load from devices is not equal to effective load from EnergyPlus due to individual load demand factors.
Note on I17: Uses device peak load instead of connected load to account for device demand factors. This column gives each device's "share" of the building's total plug load.

## Floor 2
Versioning Information
Building Category | Commercial
Building Type | Medium Office
Code/Year | ASHRAE 90.1-2019
Location | All
Floor Characteristics
Floor Number: | 2
Floor Area: | 17866.6667 | ft²
| 1659.8676 | m²
Total Receptacles: | 646
Effective Load: | 13401.9994 | W
Power Density: | 8.0741 | W/m²
Connected Plug Load
Device Type | Density (Qty. per 1000 ft²) | Number of Devices | Design Maximum | Rated Unit Power (Wrated) | Demand Factor (Wpeak/Wrated) | Connected Load (Wrated) | Effective Load (W) | Notes
Desktop computers | 0 | 0 | - | 1046 | 0.115 | 0 | 0 | Assume all desktop computers converted to laptop computers.
Laptop computers | 2.81 | 50 | 106 | 57 | 0.322 | 2850 | 917.7
Monitors | 1.87 | 33 | 106 | 46 | 0.558 | 1518 | 847.044
TVs / displays | 0.26 | 5 | 42 | 127 | 0.558 | 635 | 354.33
Copiers | 0 | 0 | - | 648 | 0.271 | 0 | 0 | NEMs density < 1 per 100,000 ft². Assume none (MFDs only).
Printers | 0.52 | 9 | - | 875 | 0.271 | 7875 | 2134.125
Multi-Function Devices | 0.17 | 3 | - | 684 | 0.271 | 2052 | 556.092
IT Equipment | 3.078 | 55 | - | 160 | 0.225 | 8800 | 1980 | NEMs density is very high; assume fewer, larger devices
Other / Empty |  | 491 | 392 |  |  |  | 6612.7084
Total |  | 646 |  |  |  | 23730 | 13401.9994
Note on C12: Per electrical circuit design
Note on C13: Connected load derived from EnergyPlus input description file (IDF); excludes elevators.
Note on C17: See Plug Load Characteristics spreadsheet
Note on E17: Maximum number of devices based on design occupancy of detailed furniture layout by PNNL team. For reference only.
Note on F17: See Plug Load Characteristics spreadsheet
Note on G17: See Plug Load Characteristics spreadsheet
Note on H17: Total connected load from devices is not equal to effective load from EnergyPlus due to individual load demand factors.
Note on I17: Uses device peak load instead of connected load to account for device demand factors. This column gives each device's "share" of the building's total plug load.

## Floor 3
Versioning Information
Building Category | Commercial
Building Type | Medium Office
Code/Year | ASHRAE 90.1-2019
Location | All
Floor Characteristics
Floor Number: | 3
Floor Area: | 17866.6667 | ft²
| 1659.8676 | m²
Total Receptacles: | 535
Effective Load: | 13401.9994 | W
Power Density: | 8.0741 | W/m²
Connected Plug Load
Device Type | Density (Qty. per 1000 ft²) | Number of Devices | Design Maximum | Rated Unit Power (Wrated) | Demand Factor (Wpeak/Wrated) | Connected Load (Wrated) | Effective Load (W) | Notes
Desktop computers | 0 | 0 | - | 1046 | 0.115 | 0 | 0 | Assume all desktop computers converted to laptop computers.
Laptop computers | 2.81 | 50 | 94 | 57 | 0.322 | 2850 | 917.7
Monitors | 1.87 | 33 | 94 | 46 | 0.558 | 1518 | 847.044
TVs / displays | 0.26 | 5 | 31 | 127 | 0.558 | 635 | 354.33
Copiers | 0 | 0 | - | 648 | 0.271 | 0 | 0 | NEMs density < 1 per 100,000 ft². Assume none (MFDs only).
Printers | 0.52 | 9 | - | 875 | 0.271 | 7875 | 2134.125
Multi-Function Devices | 0.17 | 3 | - | 684 | 0.271 | 2052 | 556.092
IT Equipment | 3.078 | 55 | - | 160 | 0.225 | 8800 | 1980 | NEMs density is very high; assume fewer, larger devices
Other / Empty |  | 380 | 316 |  |  |  | 6612.7084
Total |  | 535 |  |  |  | 23730 | 13401.9994
Note on C12: Per electrical circuit design
Note on C13: Connected load derived from EnergyPlus input description file (IDF); excludes elevators.
Note on C17: See Plug Load Characteristics spreadsheet
Note on E17: Maximum number of devices based on design occupancy of detailed furniture layout by PNNL team. For reference only.
Note on F17: See Plug Load Characteristics spreadsheet
Note on G17: See Plug Load Characteristics spreadsheet
Note on H17: Total connected load from devices is not equal to effective load from EnergyPlus due to individual load demand factors.
Note on I17: Uses device peak load instead of connected load to account for device demand factors. This column gives each device's "share" of the building's total plug load.