## Sources
Source | Citation | Notes
Barbour et al. (2017) | Barbour, Ed, Matt Guernsey, Emmanuel Anifowoshe, Seth Schober, Jay Ratafia-Brown, Peter Kobylarek, and Matt Cleaver. 2017. “Appendix B: Analysis of Commercial Miscellaneous Electric Loads - 2017 Update.” In Analysis and Representation of Miscellaneous Electric Loads in NEMS, 61. Navigant Consulting Inc. and Leidos Inc. prepared for the U.S. Energy Information Administration. https://www.eia.gov/analysis/studies/demand/miscelectric/pdf/miscelectric.pdf. | Summary of AEC, UEC, and installed base analysis for NEMS; covers devices not covered in the 2021 Appendix
Barbour et al. (2021) | Barbour, Ed, Aziz Iqbal, Michael Pan, Alejandro Valdez, Peter Kobylarek, Matt Cleaver, and John Meyer. 2021. “Appendix A: Miscellaneous Electric Load Consumption Characterization 2021 Update.” In Analysis and Representation of Miscellaneous Electric Loads in NEMS, 199. Guidehouse Inc. and Leidos Inc. prepared for the U.S. Energy Information Administration. https://www.eia.gov/analysis/studies/demand/miscelectric/pdf/miscelectric.pdf. | Summary of AEC, UEC, and installed base analysis for NEMS
CBECS 2012 Microdata | U.S. Energy Information Administration. 2012. “Commercial Buildings Energy Consumption Survey (CBECS).” 2012. https://www.eia.gov/consumption/commercial/. | Installed base source data used by NEMS; used for floor areas for calculting MELs density
Kwatra et al. (2013) | Kwatra, Sameer, Jennifer Amann, and Harvey Sachs. 2013. “Miscellaneous Energy Loads in Buildings.” Technical Report A133. Washington, D.C., USA: American Council for an Energy Efficient Economy. | Earlier study providing AEC, UEC, and installed base; included here for reference only
Navigant (2013) | Navigant Consulting and SAIC. 2013. “Analysis and Representation of Miscellaneous Electric Loads in NEMS.” 160750. Washington, D.C., USA: U.S. Energy Information Administration. https://www.eia.gov/analysis/studies/demand/miscelectric/. | Earlier study providing AEC, UEC, and installed base; included here for reference only
Santos et al. (2021) | Santos, Arthur, Gerald Duggan, Stephen Frank, Daniel Gerber, and Daniel Zimmerle. 2021. “Endpoint Use Efficiency Comparison for AC and DC Power Distribution in Commercial Buildings.” Energies 14 (18): 5863. https://doi.org/10.3390/en14185863. | Source for typical load and demand factors for office MELs
Sarfraz and Bach (2018a) | Sarfraz, Omer, and Christian K. Bach. 2018. “Equipment Power Consumption and Load Factor Profiles for Buildings’ Energy Simulation (ASHRAE 1742-RP).” Science and Technology for the Built Environment 24 (10): 1054–63. https://doi.org/10.1080/23744731.2018.1483148. | Source for typical load factors for office MELs
Sarfraz and Bach (2018b) | Sarfraz, Omer, and Christian K. Bach. 2018. “Experimental Methodology and Results for Heat Gains from Various Office Equipment (ASHRAE RP-1742).” Science and Technology for the Built Environment 24 (4): 435–47. https://doi.org/10.1080/23744731.2017.1365766. | Source for typical demand factors for office MELs

## MELs Density
|  |  | Floor Area in 2012 (1000 ft²) | [9 empty] | Sources | Notes
|  |  | Assembly | Education | Food Sales | Food Service | Health Care | Lodging | Office | Mercantile & Service | Warehouse | Other | Floor Area Source | Floor Area Notes
|  |  | 10089513 | 12239024 | 1251571 | 1819435 | 5407687 | 4446881 | 16007230 | 15978281 | 13130118 | 6706625 | CBECS 2012 Microdata | Computed directly using replicate weights; categories grouped to match Barbour et al. (2021)
Classification |  |  | Installed Base in 2012 (1000's of devices) | [9 empty] | Sources | Notes
Description | Group | Universal Device Category | Assembly | Education | Food Sales | Food Service | Healthcare | Lodging | Office | Mercantile & Service | Warehouse | Other | Installed Base Source | Installed Base Notes
Desktop computers | Office Equipment | Computer, desktop incl. integrated | 3729 | 19834 | 367 | 617 | 4080 | 1390 | 32938 | 6543 | 3297 | 2963 | Barbour et al. (2021)
Laptop computers | Small Portable Electronics | Computer, notebook | 1363 | 9123 | 96 | 249 | 782 | 2708 | 12015 | 2053 | 1097 | 872 | Barbour et al. (2021)
Monitors | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 3388 | 18300 | 328 | 564 | 3600 | 1593 | 29921 | 5894 | 2979 | 2660 | Barbour et al. (2021)
TVs / displays | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 1856 | 2935 | 1562 | 2435 | 583 | 6338 | 4217 | 4554 | 2180 | 1564 | Barbour et al. (2021) | Total of commercial "televisions" and "video displays"
Copiers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 24 | 26 | 2 | 3 | 16 | 6 | 128 | 33 | 18 | 11 | Barbour et al. (2017)
Printers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 1100 | 3000 | 200 | 400 | 1000 | 700 | 8300 | 2800 | 1400 | 700 | Barbour et al. (2017)
Multi-Function Devices | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 540 | 560 | 100 | 180 | 290 | 150 | 2700 | 1000 | 470 | 250 | Barbour et al. (2017)
IT Equipment | Small Hardwired/Networked Devices | Network equipment, modems, switches, routers, access points, etc. | 27912 | 158718 | 2539 | 4746 | 26651 | 22462 | 246406 | 47119 | 24085 | 21017 | Barbour et al. (2021)
Classification |  |  | Density in 2012 (Devices per 1000 ft²)
Description | Group | Universal Device Category | Assembly | Education | Food Sales | Food Service | Healthcare | Lodging | Office | Mercantile & Service | Warehouse | Other
Desktop computers | Office Equipment | Computer, desktop incl. integrated | 0.36959 | 1.6206 | 0.29323 | 0.33912 | 0.75448 | 0.31258 | 2.0577 | 0.40949 | 0.2511 | 0.4418
Laptop computers | Small Portable Electronics | Computer, notebook | 0.13509 | 0.7454 | 0.076704 | 0.13686 | 0.14461 | 0.60897 | 0.7506 | 0.12849 | 0.083548 | 0.13002
Monitors | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 0.33579 | 1.4952 | 0.26207 | 0.30999 | 0.66572 | 0.35823 | 1.8692 | 0.36888 | 0.22688 | 0.39662
TVs / displays | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 0.18395 | 0.23981 | 1.248 | 1.3383 | 0.10781 | 1.4253 | 0.26344 | 0.28501 | 0.16603 | 0.2332
Copiers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 0.0023787 | 0.0021244 | 0.001598 | 0.0016489 | 0.0029588 | 0.0013493 | 0.0079964 | 0.0020653 | 0.0013709 | 0.0016402
Printers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 0.10902 | 0.24512 | 0.1598 | 0.21985 | 0.18492 | 0.15741 | 0.51852 | 0.17524 | 0.10663 | 0.10437
Multi-Function Devices | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 0.053521 | 0.045755 | 0.0799 | 0.098932 | 0.053627 | 0.033732 | 0.16867 | 0.062585 | 0.035796 | 0.037277
IT Equipment | Small Hardwired/Networked Devices | Network equipment, modems, switches, routers, access points, etc. | 2.7664 | 12.9682 | 2.0287 | 2.6085 | 4.9284 | 5.0512 | 15.3934 | 2.9489 | 1.8343 | 3.1338
Note on D2: Includes Public Assembly and Religious Worship
Note on H2: Includes Inpatient Health Care, Outpatient Health Care, and Nursing
Note on J2: Includes all sizes of office building
Note on K2: Includes Enclosed Mall, Strip Shopping Mall, Retail Other Than Mall, and Service
Note on L2: Includes refrigerated and nonrefirgerated warehouses.
Note on M2: Includes Laboratory, Public Order and Safety, Vacant, and "other"

## Office Buildings
Classification |  |  | Literature Data |  |  |  |  | Calculated Data |  |  |  | Sources |  |  |  |  | Notes
Description | Group | Universal Device Category | 2020 Installed Base (devices) | UEC (kWh/yr) | Connected Hours (hrs/yr) | Load Factor (Wavg/Wpeak) | Demand Factor (Wpeak/Wrated) | AEC (TWh) | Normalized Avg. Power (W/Wrated) | Normalized UEC (kWh/yr/Wrated) | Target Power Rating (Wrated) | Installed Base Source | UEC Source | Connected Hours Source | Load Factor Source | Demand Factor Source | Installed Base Notes | UEC Notes | Connected Hours Notes | Load Factor Notes | Demand Factor Notes
Desktop computers | Office Equipment | Computer, desktop incl. integrated | 26679780 | 319 | 6567 | 0.404 | 0.115 | 8.5108 | 0.04646 | 0.3051 | 1045.5492 | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) | Sarfraz and Bach (2018a) | Santos et al. (2021)
Laptop computers | Small Portable Electronics | Computer, notebook | 15739650 | 14 | 1906 | 0.397 | 0.322 | 0.22036 | 0.12783 | 0.24365 | 57.4591 | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) | Sarfraz and Bach (2018a) | Santos et al. (2021)
Monitors | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 36503620 | 53 | 6101 | 0.34 | 0.558 | 1.9347 | 0.18972 | 1.1575 | 45.7891 | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) | Sarfraz and Bach (2018a) | Sarfraz and Bach (2018b)
TVs / displays | Displays, Entertainment, & Audio | Display incl. monitor, projectors, TVs, digital picture frame | 5313420 | 174.669 | 8760 | 0.28245 | 0.558 | 0.92809 | 0.15761 | 1.3806 | 126.5123 | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) |  | Total of commercial "televisions" and "video displays" | Weighted average of commercial "televisions" and "video displays" | Both categories of devices have no estimated "off" hours | Estimated load factor as ratio of active mode hours to total hours | No data; used monitor values
Copiers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 102400 | 180 | 8760 | 0.117 | 0.271 | 0.018432 | 0.031707 | 0.27775 | 648.0571 | Barbour et al. (2017) | Barbour et al. (2017) | [5 empty] | No data; assumed "always connected" | No data; used printer values | No data; used printer values
Printers | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 6640000 | 243 | 8760 | 0.117 | 0.271 | 1.6135 | 0.031707 | 0.27775 | 874.877 | Barbour et al. (2017) | Barbour et al. (2017) |  | Sarfraz and Bach (2018a) | Sarfraz and Bach (2018b) |  |  | No data; assumed "always connected"
Multi-Function Devices | Office Equipment | Imaging equipment fax, multi-function device, scanner, printer, label printer | 4023000 | 190 | 8760 | 0.117 | 0.271 | 0.76437 | 0.031707 | 0.27775 | 684.0602 | Barbour et al. (2017) | Barbour et al. (2017) | [5 empty] | No data; assumed "always connected" | No data; used printer values | No data; used printer values
IT Equipment | Small Hardwired/Networked Devices | Network equipment, modems, switches, routers, access points, etc. | 197124800 | 36 | 8760 | 0.573 | 0.225 | 7.0965 | 0.12892 | 1.1294 | 31.8758 | Barbour et al. (2021) | Barbour et al. (2021) | Barbour et al. (2021) | Santos et al. (2021) | Santos et al. (2021) |  |  |  | Limited number of devices sampled | Limited number of devices sampled
Note on D2: Office buildings only. Scaled from 2012 to 2020 using growth projections for all buildings.
Note on E2: Stephen Frank: UEC = Unit Energy Consumption
Note on F2: Estimated hours the device is not off or disconnected.
Note on G2: Assumed to apply only for hours where the device is not off or disconnected.
Note on I2: AEC = Annual Energy Consumption Calculated from UEC x Installed Base
Note on J2: Normalized Avg. Power = Load Factor x Demand Factor This applies only to connected hours
Note on K2: Calculated from the number of connected hours per year and the normalize average power.
Note on L2: This value is an input power rating because it represents both the DC load and the load-packaged converter loss.

## Data ¦ Desktops
Source: Sarfraz and Bach (2018a) Table 3 |  |  | Source: Santos et al. (2021) Table 3 |  | Source: Barbour et al. (2021) Slide 87
Description: 30-Min average heat gains normalized by equipment peak heat gain [Desktops] |  |  | Description: Appliances’ converter power level distribution (% of rated load). [Desktops] |  | Description: Commercial Desktop PCs
Interpretation: This table can be used to calculate typical load factor (average load / peak load) |  |  | Interpretation: This table directly provides the demand factor (peak load / connected load) and can also be used to calculate typical load factor (average load / peak load). However, Table 3 only included data when the device was "on" (drawing more than 1W), so the load factor may be skewed high. |  | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Time Interval | Weekdays | Weekends | Statistic | Value (% of Rated Load) | Year | Installed Base | Multiplier
0:00–0:30 | 0.34 | 0.29 | Minimum | 0.2% | 2012 | 75757000 | 1
0:30–1:00 | 0.34 | 0.3 | Lower quartile | 4.6% | 2015 | 72424000 | 0.956
1:00–1:30 | 0.34 | 0.3 | Median | 7% | 2018 | 68845000 | 0.90876
1:30–2:00 | 0.35 | 0.31 | Mean | 7.3% | 2020 | 61161000 | 0.80733
2:00–2:30 | 0.35 | 0.3 | Upper Quartile | 11.5% | 2030 | 50080000 | 0.66106
2:30–3:00 | 0.36 | 0.31 | Maximum | 11.5% | 2040 | 38142000 | 0.50348
3:00–3:30 | 0.35 | 0.31 | Load Factor (Wavg/Wpeak) [On State Only] | 0.63478 | 2050 | 29003000 | 0.38284
3:30–4:00 | 0.35 | 0.3 | Demand Factor (Wpeak/Wrated) | 0.115
4:00–4:30 | 0.35 | 0.3
4:30–5:00 | 0.34 | 0.3
5:00–5:30 | 0.34 | 0.3
5:30–6:00 | 0.34 | 0.3
6:00–6:30 | 0.35 | 0.3
6:30–7:00 | 0.39 | 0.3
7:00–7:30 | 0.46 | 0.3
7:30–8:00 | 0.54 | 0.3
8:00–8:30 | 0.56 | 0.3
8:30–9:00 | 0.59 | 0.3
9:00–9:30 | 0.6 | 0.31
9:30–10:00 | 0.61 | 0.32
10:00–10:30 | 0.63 | 0.32
10:30–11:00 | 0.62 | 0.32
11:00–11:30 | 0.6 | 0.32
11:30–12:00 | 0.59 | 0.32
12:00–12:30 | 0.59 | 0.32
12:30–13:00 | 0.61 | 0.32
13:00–13:30 | 0.61 | 0.33
13:30–14:00 | 0.6 | 0.33
14:00–14:30 | 0.6 | 0.33
14:30–15:00 | 0.6 | 0.32
15:00–15:30 | 0.61 | 0.32
15:30–16:00 | 0.58 | 0.32
16:00–16:30 | 0.52 | 0.31
16:30–17:00 | 0.44 | 0.31
17:00–17:30 | 0.4 | 0.31
17:30–18:00 | 0.37 | 0.31
18:00–18:30 | 0.36 | 0.3
18:30–19:00 | 0.34 | 0.3
19:00–19:30 | 0.34 | 0.3
19:30–20:00 | 0.34 | 0.3
20:00–20:30 | 0.34 | 0.3
20:30–21:00 | 0.33 | 0.3
21:00–21:30 | 0.33 | 0.3
21:30–22:00 | 0.33 | 0.3
22:00–22:30 | 0.33 | 0.3
22:30–23:00 | 0.33 | 0.3
23:00–23:30 | 0.32 | 0.3
23:30–24:00 | 0.32 | 0.3
Average Load Factor | 0.44229 | 0.3075
Weighted Average (All Days) | 0.40378

## Data ¦ Laptops
Source: Sarfraz and Bach (2018a) Table 3 |  |  | Source: Santos et al. (2021) Table 3 |  | Source: Barbour et al. (2021) Slide 85
Description: 30-Min average heat gains normalized by equipment peak heat gain [Laptops] |  |  | Description: Appliances’ converter power level distribution (% of rated load). [Laptops] |  | Description: Commercial Laptop PCs
Interpretation: This table can be used to calculate typical load factor (average load / peak load) |  |  | Interpretation: This table directly provides the demand factor (peak load / connected load) and can also be used to calculate typical load factor (average load / peak load). However, Table 3 only included data when the device was "on" (drawing more than 1W), so the load factor may be skewed high. |  | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Time Interval | Weekdays | Weekends | Statistic | Value (% of Rated Load) | Year | Installed Base | Multiplier
0:00–0:30 | 0.31 | 0.33 | Minimum | 4.4% | 2012 | 30358000 | 1
0:30–1:00 | 0.31 | 0.33 | Lower quartile | 10% | 2015 | 34803000 | 1.1464
1:00–1:30 | 0.31 | 0.33 | Median | 13.3% | 2018 | 39673000 | 1.3068
1:30–2:00 | 0.32 | 0.33 | Mean | 18.2% | 2020 | 39782000 | 1.3104
2:00–2:30 | 0.32 | 0.33 | Upper Quartile | 31.1% | 2030 | 59680000 | 1.9659
2:30–3:00 | 0.32 | 0.35 | Maximum | 32.2% | 2040 | 83274000 | 2.7431
3:00–3:30 | 0.33 | 0.35 | Load Factor (Wavg/Wpeak) [On State Only] | 0.56522 | 2050 | 116011000 | 3.8214
3:30–4:00 | 0.32 | 0.35 | Demand Factor (Wpeak/Wrated) | 0.322
4:00–4:30 | 0.32 | 0.35
4:30–5:00 | 0.32 | 0.34
5:00–5:30 | 0.32 | 0.34
5:30–6:00 | 0.33 | 0.34
6:00–6:30 | 0.35 | 0.34
6:30–7:00 | 0.42 | 0.34
7:00–7:30 | 0.46 | 0.35
7:30–8:00 | 0.49 | 0.34
8:00–8:30 | 0.51 | 0.34
8:30–9:00 | 0.53 | 0.34
9:00–9:30 | 0.56 | 0.35
9:30–10:00 | 0.53 | 0.35
10:00–10:30 | 0.53 | 0.34
10:30–11:00 | 0.53 | 0.33
11:00–11:30 | 0.52 | 0.33
11:30–12:00 | 0.56 | 0.33
12:00–12:30 | 0.58 | 0.33
12:30–13:00 | 0.6 | 0.33
13:00–13:30 | 0.57 | 0.34
13:30–14:00 | 0.57 | 0.33
14:00–14:30 | 0.55 | 0.34
14:30–15:00 | 0.54 | 0.34
15:00–15:30 | 0.54 | 0.34
15:30–16:00 | 0.5 | 0.34
16:00–16:30 | 0.46 | 0.34
16:30–17:00 | 0.45 | 0.34
17:00–17:30 | 0.42 | 0.33
17:30–18:00 | 0.39 | 0.34
18:00–18:30 | 0.37 | 0.34
18:30–19:00 | 0.38 | 0.38
19:00–19:30 | 0.38 | 0.33
19:30–20:00 | 0.36 | 0.33
20:00–20:30 | 0.34 | 0.33
20:30–21:00 | 0.34 | 0.33
21:00–21:30 | 0.34 | 0.34
21:30–22:00 | 0.34 | 0.34
22:00–22:30 | 0.34 | 0.34
22:30–23:00 | 0.34 | 0.34
23:00–23:30 | 0.34 | 0.33
23:30–24:00 | 0.34 | 0.33
Average Load Factor | 0.42083 | 0.33854
Weighted Average (All Days) | 0.39732

## Data ¦ Monitors
Source: Sarfraz and Bach (2018a) Table 3 |  |  | Source: Sarfraz and Bach (2018b) Table 8 |  |  |  |  | Source: Santos et al. (2021) Table 3 |  | Source: Barbour et al. (2021) Slide 85
Description: 30-Min average heat gains normalized by equipment peak heat gain [Screens] |  |  | Description: Recommended heat gain for typical screens |  |  |  |  | Description: Appliances’ converter power level distribution (% of rated load). [Monitors] |  | Description: Commercial PC Monitors
Interpretation: This table can be used to calculate typical load factor (average load / peak load) |  |  | Interpretation: This table gives nameplate power and peak demand power for monitors; it can be used to derive typical demand factors (peak load / connected load). |  |  |  |  | Interpretation: This table directly provides the demand factor (peak load / connected load) and can also be used to calculate typical load factor (average load / peak load). However, Table 3 only included data when the device was "on" (drawing more than 1W), so the load factor may be skewed high. |  | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Time Interval | Weekdays | Weekends | Equipment Description | Qty Tested | Nameplate Power (W) | Peak Power (W) | Demand Factor (Wpeak/Wrated) | Statistic | Value (% of Rated Load) | Year | Installed Base | Multiplier
0:00–0:30 | 0.23 | 0.21 | Monitor Manufacturer U (model A); 1397 mm LED Flat screen | 1 | 240 | 50 | 0.20833 | Minimum | 16.8% | 2012 | 70746000 | 1
0:30–1:00 | 0.22 | 0.21 | Manufacturer U (model B); 686 mm LCD Flat screen | 2 | 40 | 26 | 0.65 | Lower quartile | 34.3% | 2015 | 79058000 | 1.1175
1:00–1:30 | 0.22 | 0.21 | Manufacturer U (model C); 546 mm LED Flat screen | 2 | 29 | 25 | 0.86207 | Median | 40.5% | 2018 | 87875000 | 1.2421
1:30–2:00 | 0.22 | 0.19 | Manufacturer V (model A); 1270 mm 3D LED Flat screen | 1 | 94 | 49 | 0.52128 | Mean | 39.8% | 2020 | 86662000 | 1.225
2:00–2:30 | 0.22 | 0.19 | Manufacturer W (model A); 864 mm LCD curved screen | 1 | 130 | 48 | 0.36923 | Upper Quartile | 47.4% | 2030 | 78330000 | 1.1072
2:30–3:00 | 0.22 | 0.19 | Manufacturer W (model B); 584 mm LED Flat screen | 3 | 50 | 17 | 0.34 | Maximum | 66.7% | 2040 | 71095000 | 1.0049
3:00–3:30 | 0.22 | 0.19 | Manufacturer W (model C); 584 mm LED Flat screen | 1 | 38 | 21 | 0.55263 | Load Factor (Wavg/Wpeak) [On State Only] | 0.5967 | 2050 | 71790000 | 1.0148
3:30–4:00 | 0.22 | 0.19 | Manufacturer W (model D); 584 mm LED Flat screen | 1 | 38 | 14 | 0.36842 | Demand Factor (Wpeak/Wrated) | 0.667
4:00–4:30 | 0.22 | 0.19 | Manufacturer X (model A); 610 mm LCD Flat screen | 1 | 42 | 25 | 0.59524
4:30–5:00 | 0.22 | 0.19 | Manufacturer Y (model A); 600 mm LED Flat screen | 1 | 26 | 17 | 0.65385
5:00–5:30 | 0.22 | 0.19 | Manufacturer Y (model B); 546 mm LCD Flat screen | 1 | 29 | 22 | 0.75862
5:30–6:00 | 0.23 | 0.19 | Manufacturer Z (model A); 546 mm LED Flat screen | 1 | 28 | 24 | 0.85714
6:00–6:30 | 0.31 | 0.19 | Weighted Average Demand Factor |  |  |  | 0.55805
6:30–7:00 | 0.38 | 0.19
7:00–7:30 | 0.4 | 0.19
7:30–8:00 | 0.53 | 0.19
8:00–8:30 | 0.62 | 0.19
8:30–9:00 | 0.65 | 0.19
9:00–9:30 | 0.64 | 0.19
9:30–10:00 | 0.63 | 0.19
10:00–10:30 | 0.63 | 0.19
10:30–11:00 | 0.65 | 0.19
11:00–11:30 | 0.67 | 0.19
11:30–12:00 | 0.65 | 0.19
12:00–12:30 | 0.61 | 0.19
12:30–13:00 | 0.61 | 0.19
13:00–13:30 | 0.66 | 0.19
13:30–14:00 | 0.65 | 0.19
14:00–14:30 | 0.66 | 0.19
14:30–15:00 | 0.64 | 0.19
15:00–15:30 | 0.62 | 0.19
15:30–16:00 | 0.57 | 0.21
16:00–16:30 | 0.53 | 0.2
16:30–17:00 | 0.48 | 0.19
17:00–17:30 | 0.4 | 0.19
17:30–18:00 | 0.33 | 0.19
18:00–18:30 | 0.3 | 0.2
18:30–19:00 | 0.28 | 0.2
19:00–19:30 | 0.28 | 0.19
19:30–20:00 | 0.28 | 0.2
20:00–20:30 | 0.26 | 0.21
20:30–21:00 | 0.23 | 0.22
21:00–21:30 | 0.22 | 0.19
21:30–22:00 | 0.22 | 0.2
22:00–22:30 | 0.22 | 0.2
22:30–23:00 | 0.22 | 0.19
23:00–23:30 | 0.22 | 0.19
23:30–24:00 | 0.23 | 0.19
Average Load Factor | 0.39875 | 0.19396
Weighted Average (All Days) | 0.34024

## Data ¦ TVs
Source: Barbour et al. (2021) Slide 113 |  |  | Source: Barbour et al. (2021) Slide 115
Description: Commercial Televisions |  |  | Description: Video Displays
Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type. |  |  | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Year | Installed Base | Multiplier | Year | Installed Base | Multiplier
2012 | 19194000 | 1 | 2012 | 9028000 | 1
2015 | 20926000 | 1.0902 | 2015 | 9843000 | 1.0903
2018 | 22815000 | 1.1887 | 2018 | 10731000 | 1.1886
2020 | 24169000 | 1.2592 | 2020 | 11368000 | 1.2592
2030 | 30909000 | 1.6103 | 2030 | 15163000 | 1.6796
2040 | 34006000 | 1.7717 | 2040 | 16592000 | 1.8378
2050 | 37269000 | 1.9417 | 2050 | 18156000 | 2.0111

## Data ¦ Copiers
Source: Barbour et al. (2017) Slide 34
Description: Office MELs >> Copier
Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Year | Installed Base | Multiplier
2012 | 270000 | 1
2016 | 240000 | 0.88889
2020 | 190000 | 0.7037
2030 | 100000 | 0.37037
2040 | 50000 | 0.18519
2050 | 30000 | 0.11111

## Data ¦ Printers
Source: Sarfraz and Bach (2018a) Table 3 |  |  | Source: Sarfraz and Bach (2018b) Table 9 | [5 empty] | Source: Barbour et al. (2017) Slide 42
Description: 30-Min average heat gains normalized by equipment peak heat gain [Printers] |  |  | Description: Recommended heat gain for typical printers | [5 empty] | Description: Office MELs >> Printer
Interpretation: This table can be used to calculate typical load factor (average load / peak load) |  |  | Interpretation: This table gives nameplate power and peak demand power for printers, including multifunction devices (the modern version of copiers). It can be used to derive typical demand factors (peak load / connected load) for copiers and printers. | [5 empty] | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Time Interval | Weekdays | Weekends | Equipment Description |  | Qty Tested | Nameplate Power (W) | Peak Power (W) | Demand Factor (Wpeak/Wrated) | Year | Installed Base | Multiplier
0:00–0:30 | 0.06 | 0.07 | Multi-function printer (copy, print, scan) | Large, multi-user, office type | 1 | 1010 | 540 | 0.53465 | 2012 | 20000000 | 1
0:30–1:00 | 0.06 | 0.07 | Multi-function printer (copy, print, scan) | Large, multi-user, office type | 1 | 1300 | 303 | 0.23308 | 2016 | 17000000 | 0.85
1:00–1:30 | 0.06 | 0.07 | Multi-function printer (copy, print, scan) | Large, multi-user, office type | 1 | 1500 | 433 | 0.28867 | 2020 | 13000000 | 0.65
1:30–2:00 | 0.06 | 0.07 | Monochrome printer | Medium, multi-user, office type | 1 | 900 | 732 | 0.81333 | 2030 | 7000000 | 0.35
2:00–2:30 | 0.06 | 0.07 | Monochrome printer | Typical desktop, small-office type | 1 | 470 | 56 | 0.11915 | 2040 | 4000000 | 0.2
2:30–3:00 | 0.07 | 0.08 | Monochrome printer | Typical desktop, medium-office type | 1 | 1000 | 222 | 0.222 | 2050 | 3000000 | 0.15
3:00–3:30 | 0.07 | 0.08 | Monochrome printer | Typical desktop, medium-office type | 1 | 680 | 61 | 0.089706
3:30–4:00 | 0.06 | 0.07 | Color printer | Typical desktop, medium-office type | 1 | 620 | 120 | 0.19355
4:00–4:30 | 0.06 | 0.07 | Laser printer | Typical desktop, small-office type | 1 | 310 | 89 | 0.2871
4:30–5:00 | 0.06 | 0.06 | Laser printer | Typical desktop, small-office type | 1 | 495 | 67 | 0.13535
5:00–5:30 | 0.06 | 0.07 | Laser printer | Typical desktop, small-office type | 1 | 1090 | 65 | 0.059633
5:30–6:00 | 0.07 | 0.07 | Weighted Average Demand Factor |  |  |  |  | 0.27057
6:00–6:30 | 0.08 | 0.08
6:30–7:00 | 0.16 | 0.1
7:00–7:30 | 0.2 | 0.08
7:30–8:00 | 0.2 | 0.09
8:00–8:30 | 0.19 | 0.1
8:30–9:00 | 0.26 | 0.09
9:00–9:30 | 0.24 | 0.09
9:30–10:00 | 0.21 | 0.09
10:00–10:30 | 0.22 | 0.11
10:30–11:00 | 0.21 | 0.09
11:00–11:30 | 0.19 | 0.09
11:30–12:00 | 0.2 | 0.1
12:00–12:30 | 0.25 | 0.13
12:30–13:00 | 0.2 | 0.08
13:00–13:30 | 0.16 | 0.13
13:30–14:00 | 0.19 | 0.15
14:00–14:30 | 0.19 | 0.12
14:30–15:00 | 0.17 | 0.17
15:00–15:30 | 0.16 | 0.15
15:30–16:00 | 0.17 | 0.11
16:00–16:30 | 0.16 | 0.13
16:30–17:00 | 0.14 | 0.11
17:00–17:30 | 0.12 | 0.13
17:30–18:00 | 0.09 | 0.09
18:00–18:30 | 0.09 | 0.1
18:30–19:00 | 0.1 | 0.13
19:00–19:30 | 0.1 | 0.1
19:30–20:00 | 0.09 | 0.09
20:00–20:30 | 0.09 | 0.07
20:30–21:00 | 0.08 | 0.08
21:00–21:30 | 0.08 | 0.07
21:30–22:00 | 0.07 | 0.09
22:00–22:30 | 0.07 | 0.08
22:30–23:00 | 0.06 | 0.07
23:00–23:30 | 0.06 | 0.08
23:30–24:00 | 0.06 | 0.07
Average Load Factor | 0.12625 | 0.093542
Weighted Average (All Days) | 0.1169

## Data ¦ MFDs
Source: Barbour et al. (2017) Slide 38
Description: Office MELs >> MFD
Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Year | Installed Base | Multiplier
2012 | 6300000 | 1
2016 | 8500000 | 1.3492
2020 | 9400000 | 1.4921
2030 | 13000000 | 2.0635
2040 | 17000000 | 2.6984
2050 | 23000000 | 3.6508

## Data ¦ IT Equipment
Source: Santos et al. (2021) Table 3 |  | Source: Barbour et al. (2021) Slide 93
Description: Appliances’ converter power level distribution (% of rated load). [IT Equipment] |  | Description: IT equipment
Interpretation: This table directly provides the demand factor (peak load / connected load) and can also be used to calculate typical load factor (average load / peak load). However, Table 3 only included data when the device was "on" (drawing more than 1W), so the load factor may be skewed high. |  | Interpretation: This table provides overall installed base by year, which can be used for growth projections. The table on the following slide provides estimates of 2012 installed base by building type.
Statistic | Value (% of Rated Load) | Year | Installed Base | Multiplier
Minimum | 2.8% | 2012 | 581654000 | 1
Lower quartile | 5.6% | 2015 | 472000000 | 0.81148
Median | 5.6% | 2018 | 466123000 | 0.80138
Mean | 12.9% | 2020 | 466398000 | 0.80185
Upper Quartile | 21.5% | 2030 | 594836000 | 1.0227
Maximum | 22.5% | 2040 | 712781000 | 1.2254
Load Factor (Wavg/Wpeak) [On State Only] | 0.57333 | 2050 | 909102000 | 1.563
Demand Factor (Wpeak/Wrated) | 0.225