## AC-DC Converters
Device Metadata |  |  |  | Device Ratings |  |  | Characterization Metadata |  |  |  | Output Configuration |  |  | Efficiency Curve Data | [9 empty] | Other
Manufacturer | Model | Description | Type | Rated Voltage Input (V) | Rated Voltage Output (V) | Rated Power Output (W) | Efficiency Data Source | Harmonics Data Source | Data Directory | Harmonics Group Column | Disambiguation Suffix | Model Label | Use? | Eff @ 10% | Eff @ 20% | Eff @ 30% | Eff @ 40% | Eff @ 50% | Eff @ 60% | Eff @ 70% | Eff @ 80% | Eff @ 90% | Eff @ 100% | Notes | Issues
Apple | A1385 | AC/DC USB Charger | SISO | 120 | 5 | 5 | Laboratory Characterization | Laboratory Characterization | AC-DC Apple A1385 USB (iPhone) Charger | Power Step |  | Apple-A1385 | Y
Charging Essentials | LA-5A-4 | AC/DC USB Charger | SIMO | 125 | 5 | 4.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Charging Essentials LA-5A-4 USB Charger (Port 1) | Power Step | Port1 | Charging-Essentials-LA-5A-4-Port1 | Y | [10 empty] | Each port characterized independently
Charging Essentials | LA-5A-4 | AC/DC USB Charger | SIMO | 125 | 5 | 4.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Charging Essentials LA-5A-4 USB Charger (Port 2) | Power Step | Port2 | Charging-Essentials-LA-5A-4-Port2 | N | [10 empty] | Each port characterized independently
Charging Essentials | LA-5A-4 | AC/DC USB Charger | SIMO | 125 | 5 | 4.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Charging Essentials LA-5A-4 USB Charger (Port 3) | Power Step | Port3 | Charging-Essentials-LA-5A-4-Port3 | N | [10 empty] | Each port characterized independently
Charging Essentials | LA-5A-4 | AC/DC USB Charger | SIMO | 125 | 5 | 4.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Charging Essentials LA-5A-4 USB Charger (Port 4) | Power Step | Port4 | Charging-Essentials-LA-5A-4-Port4 | N | [10 empty] | Each port characterized independently
Cisco | CDB-8U | AC/DC PoE Switch | SIMO | 120 | 48 | 480 | Laboratory Characterization | Laboratory Characterization | AC-DC Cisco CDB-8U PoE Switch | Power Step |  | Cisco-CDB-8U | Y | [10 empty] | Data obtained from Anay Waghale at PNNL
DELL | DA90PE1-00 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC DELL DA90PE1-00 Laptop Power Supply | Power Step |  | DELL-DA90PE1-00 | Y
DELL | PA-10 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC DELL PA-10 Laptop Power Supply | Power Step |  | DELL-PA-10 | Y | [10 empty] | Use as representative harmonic spectrum for 40W < P <= 120W
Delta | LNE-48V100W | AC/DC LED Driver | SISO | 115 | 48 | 100 | Datasheet | NA |  |  | 115V | Delta-LNE-48V100W-115V | Y | 0.72528 | 0.83503 | 0.88113 | 0.9011 | 0.91061 | 0.91657 | 0.9206 | 0.9206 | 0.92012 | 0.92202
Delta | LNE-48V100W | AC/DC LED Driver | SISO | 277 | 48 | 100 | Datasheet | NA |  |  | 277V | Delta-LNE-48V100W-277V | Y | 0.75267 | 0.81029 | 0.8721 | 0.89017 | 0.90443 | 0.90538 | 0.9187 | 0.9244 | 0.92916 | 0.93296
Delta | LNE-48V120W | AC/DC LED Driver | SISO | 115 | 48 | 120 | Datasheet | NA |  |  | 115V | Delta-LNE-48V120W-115V | Y | 0.72553 | 0.87147 | 0.9008 | 0.91249 | 0.91773 | 0.92037 | 0.92131 | 0.92214 | 0.92131 | 0.91964
Delta | LNE-48V120W | AC/DC LED Driver | SISO | 277 | 48 | 120 | Datasheet | NA |  |  | 277V | Delta-LNE-48V120W-277V | Y | 0.73674 | 0.85883 | 0.89079 | 0.90366 | 0.91058 | 0.92107 | 0.92846 | 0.93371 | 0.93609 | 0.93848
Delta | LNE-48V150W | AC/DC LED Driver | SISO | 115 | 48 | 150 | Datasheet | NA |  |  | 115V | Delta-LNE-48V150W-115V | Y | 0.71507 | 0.84884 | 0.88497 | 0.8978 | 0.90778 | 0.9129 | 0.91349 | 0.91682 | 0.91587 | 0.91587
Delta | LNE-48V150W | AC/DC LED Driver | SISO | 277 | 48 | 150 | Datasheet | NA |  |  | 277V | Delta-LNE-48V150W-277V | Y | 0.73761 | 0.84314 | 0.87784 | 0.894 | 0.90161 | 0.91206 | 0.92109 | 0.92727 | 0.93155 | 0.93345
Delta | LNE-48V185W | AC/DC LED Driver | SISO | 115 | 48 | 185 | Datasheet | NA |  |  | 115V | Delta-LNE-48V185W-115V | Y | 0.75988 | 0.86861 | 0.8927 | 0.90748 | 0.91225 | 0.9175 | 0.91803 | 0.91893 | 0.91559 | 0.91416
Delta | LNE-48V185W | AC/DC LED Driver | SISO | 277 | 48 | 185 | Datasheet | NA |  |  | 277V | Delta-LNE-48V185W-277V | Y | 0.76322 | 0.85621 | 0.88912 | 0.89794 | 0.91392 | 0.9256 | 0.93037 | 0.93514 | 0.93562 | 0.93705
Delta | LNE-54V150W | AC/DC LED Driver | SISO | 115 | 54 | 150 | Datasheet | NA |  |  | 115V | Delta-LNE-54V150W-115V | Y | 0.76552 | 0.8641 | 0.88994 | 0.90621 | 0.91147 | 0.91555 | 0.91626 | 0.91722 | 0.91723 | 0.91722
Delta | LNE-54V150W | AC/DC LED Driver | SISO | 277 | 54 | 150 | Datasheet | NA |  |  | 277V | Delta-LNE-54V150W-277V | Y | 0.77079 | 0.85836 | 0.88563 | 0.89855 | 0.90382 | 0.9153 | 0.92296 | 0.92774 | 0.92966 | 0.93444
Delta | LNE-54V185W | AC/DC LED Driver | SISO | 115 | 54 | 185 | Datasheet | NA |  |  | 115V | Delta-LNE-54V185W-115V | Y | 0.80562 | 0.88038 | 0.90064 | 0.9129 | 0.91617 | 0.92047 | 0.9192 | 0.91776 | 0.91586 | 0.91586
Delta | LNE-54V185W | AC/DC LED Driver | SISO | 277 | 54 | 185 | Datasheet | NA |  |  | 277V | Delta-LNE-54V185W-277V | Y | 0.8034 | 0.86925 | 0.89279 | 0.90281 | 0.91761 | 0.92588 | 0.93081 | 0.93415 | 0.9359 | 0.93606
Delta Electronics | PMC-12V100W1AA | AC/DC Power Supply | SISO | 120 | 12 | 100 | Laboratory Characterization | Laboratory Characterization | AC-DC Delta Electronics PMC-12V100W1AA Power Supply | Fractional Load (%) |  | Delta-Electronics-PMC-12V100W1AA | Y
Delta Electronics | PMC-24V100W1AA | AC/DC Power Supply | SISO | 120 | 24 | 100 | Laboratory Characterization | Laboratory Characterization | AC-DC Delta Electronics PMC-24V100W1AA Power Supply | Fractional Load (%) |  | Delta-Electronics-PMC-24V100W1AA | Y
EDACPOWER ELEC. | EA1024F2-090 | AC/DC External Power Supply | SISO | 120 | 9 | 27 | Laboratory Characterization | Laboratory Characterization | AC-DC EDACPOWER ELEC EA1024F2-090 Power Supply | Power Step |  | EDACPOWER-ELEC.-EA1024F2-090 | Y | [10 empty] | Use as representative harmonic spectrum for 10W < P <= 40W
Emerson | Netsure 4015 | AC/DC Power Supply | SISO | 480 | 380 | 30000 | Datasheet | NA |  |  |  | Emerson-Netsure-4015 | Y | 0.94968 | 0.969 | 0.974 | 0.97567 | 0.97833 | 0.97767 | 0.97767 | 0.977 | 0.97567 | 0.975
Emerson | Netsure 9500 | AC/DC Power Supply | SISO | 480 | 380 | 120000 | Datasheet | NA |  |  |  | Emerson-Netsure-9500 | Y | 0.90317 | 0.95189 | 0.96501 | 0.97126 | 0.97345 | 0.97438 | 0.97407 | 0.97313 | 0.97095 | 0.96907
Emerson | R400-15000e | AC/DC Power Supply | SISO | 480 | 380 | 15000 | Datasheet | NA |  |  |  | Emerson-R400-15000e | Y | 0.9448 | 0.9613 | 0.9661 | 0.9683 | 0.9694 | 0.9691 | 0.9693 | 0.9694 | 0.9683 | 0.9672
Emerson | R48-12000e | AC/DC Power Supply | SISO | 480 | 48 | 11600 | Datasheet | NA |  |  |  | Emerson-R48-12000e | Y | 0.9129 | 0.9415 | 0.9516 | 0.9571 | 0.9594 | 0.96 | 0.9604 | 0.9594 | 0.9579 | 0.9559
Emerson | R48-2000e | AC/DC Power Supply | SISO | 120 | 48 | 2000 | Datasheet | NA |  |  |  | Emerson-R48-2000e | Y | 0.9023 | 0.9509 | 0.9604 | 0.9612 | 0.9604 | 0.961 | 0.9585 | 0.9562 | 0.9562 | 0.9524
Emerson | R48-3200e | AC/DC Power Supply | SISO | 240 | 48 | 3200 | Datasheet | NA |  |  |  | Emerson-R48-3200e | Y | 0.94011 | 0.95763 | 0.96616 | 0.96818 | 0.96818 | 0.96647 | 0.96383 | 0.96089 | 0.95748 | 0.95495
Emerson | R48-3500e | AC/DC Power Supply | SISO | 240 | 48 | 3500 | Datasheet | NA |  |  |  | Emerson-R48-3500e | Y | 0.9339 | 0.9528 | 0.9624 | 0.9656 | 0.966 | 0.9659 | 0.964 | 0.9619 | 0.9571 | 0.9518
Emerson | R48-5800e | AC/DC Power Supply | SISO | 480 | 48 | 5800 | Datasheet | NA |  |  |  | Emerson-R48-5800e | Y | 0.898 | 0.9376 | 0.9526 | 0.9593 | 0.9634 | 0.9647 | 0.9647 | 0.9641 | 0.9634 | 0.9624
HP | 391174-001 | AC/DC Laptop Power Supply | SISO | 120 | 18.5 | 120 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 391174-001 Laptop Power Supply | Power Step |  | HP-391174-001 | Y | [10 empty] | AC/DC laptop power supply (1 of 3, phase A) in BEEAM AC validation experiments
HP | 608425-001 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 65 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 608425-001 Laptop Power Supply | Power Step |  | HP-608425-001 | Y
HP | 608428-002 | AC/DC Laptop Power Supply | SISO | 120 | 19 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 608428-002 Laptop Power Supply | Power Step |  | HP-608428-002 | Y | [10 empty] | AC/DC laptop power supply (2 of 2) in BEEAM bench-scale co-simulation validation experiment
HP | 677774-001 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 65 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 677774-001 Laptop Power Supply | Power Step |  | HP-677774-001 | Y
HP | 677777-002 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 677777-002 Laptop Power Supply | Power Step |  | HP-677777-002 | Y | [10 empty] | AC/DC laptop power supply (1 of 2) in BEEAM bench-scale co-simulation validation experiment
HP | 740015-002 | AC/DC Laptop Power Supply | SISO | 120 | 19.5 | 45 | Laboratory Characterization | Laboratory Characterization | AC-DC HP 740015-002 Laptop Power Supply | Power Step |  | HP-740015-002 | Y
HP | PA-1121-12H | AC/DC Laptop Power Supply | SISO | 120 | 18.5 | 120 | Laboratory Characterization | Laboratory Characterization | AC-DC HP PA-1121-12H Laptop Power Supply | Power Step |  | HP-PA-1121-12H | Y | [10 empty] | AC/DC laptop power supply (3 of 3, phase C) in BEEAM AC validation experiments
HP | PA-1900-15C2 | AC/DC Laptop Power Supply | SISO | 120 | 18.5 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC HP PA-1900-15C2 Laptop Power Supply | Power Step |  | HP-PA-1900-15C2 | Y | [10 empty] | AC/DC laptop power supply (2 of 3, phase B) in BEEAM AC validation experiments
Integrated Power Designs | GRN-110-4003-CHCO | AC/DC Power Supply | SIMO | 120 | 24 | 110 | Laboratory Characterization | Laboratory Characterization | AC-DC Integrated Power Designs GRN-110-4003-CHCO Power Supply | Fractional Load (%) |  | Integrated-Power-Designs-GRN-110-4003-CHCO | Y | [10 empty] | 5V, 12V, 24V
Integrated Power Designs | REL-185-4001-CHCO | AC/DC Power Supply | SIMO | 120 | 12 | 185 | Laboratory Characterization | Laboratory Characterization | AC-DC Integrated Power Designs REL-185-4001-CHCO Power Supply | Fractional Load (%) |  | Integrated-Power-Designs-REL-185-4001-CHCO | Y | [10 empty] | 3.3V, 5V, 12V
Integrated Power Designs | REL-70-4006-CHCO | AC/DC Power Supply | SIMO | 120 | 24 | 70 | Laboratory Characterization | Laboratory Characterization | AC-DC Integrated Power Designs REL-70-4006-CHCO Power Supply | Fractional Load (%) |  | Integrated-Power-Designs-REL-70-4006-CHCO | Y | [10 empty] | 5V, 12V, 24V
LG | STA-U17WS | AC/DC USB Charger | SISO | 120 | 5.1 | 3.57 | Laboratory Characterization | Laboratory Characterization | AC-DC LG STA-U17WS USB Charger | Power Step |  | LG-STA-U17WS | Y
LG | STA-U34WVI | AC/DC USB Charger | SISO | 120 | 5.1 | 3.57 | Laboratory Characterization | Laboratory Characterization | AC-DC LG STA-U34WVI USB Charger (Device 1) | Power Step | 1 | LG-STA-U34WVI-1 | Y
LG | STA-U34WVI | AC/DC USB Charger | SISO | 120 | 5.1 | 3.57 | Laboratory Characterization | Laboratory Characterization | AC-DC LG STA-U34WVI USB Charger (Device 2) | Power Step | 2 | LG-STA-U34WVI-2 | N
Liteon | PA-1400-02 | AC/DC Laptop Power Supply | SISO | 120 | 12 | 40 | Laboratory Characterization | Laboratory Characterization | AC-DC Liteon PA-1400-02 Laptop Power Supply | Power Step |  | Liteon-PA-1400-02 | Y
Mean Well | APV-25-24 | AC/DC LED Driver | SISO | 120 | 24 | 25.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well APV-25-24 LED Driver (Device 1) | Power Step | 1 | Mean-Well-APV-25-24-1 | Y | [10 empty] | AC/DC LED driver (1 of 3, phase A) in BEEAM AC validation experiments
Mean Well | APV-25-24 | AC/DC LED Driver | SISO | 120 | 24 | 25.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well APV-25-24 LED Driver (Device 2) | Power Step | 2 | Mean-Well-APV-25-24-2 | N | [10 empty] | AC/DC LED driver (2 of 3, phase B) in BEEAM AC validation experiments
Mean Well | APV-25-24 | AC/DC LED Driver | SISO | 120 | 24 | 25.2 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well APV-25-24 LED Driver (Device 3) | Power Step | 3 | Mean-Well-APV-25-24-3 | N | [10 empty] | AC/DC LED driver (3 of 3, phase C) in BEEAM AC validation experiments
Mean Well | IRM-30-12ST | AC/DC Power Supply | SISO | 120 | 12 | 30 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well IRM-30-12ST Power Supply | Fractional Load (%) |  | Mean-Well-IRM-30-12ST | Y
Mean Well | IRM-30-24ST | AC/DC Power Supply | SISO | 120 | 24 | 30 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well IRM-30-24ST Power Supply | Power Step |  | Mean-Well-IRM-30-24ST | Y
Mean Well | RSP-1000-48 | AC/DC Power Supply | SISO | 120 | 48 | 1000 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well RSP-1000-48 Power Supply | Power Step |  | Mean-Well-RSP-1000-48 | Y | [10 empty] | AC/DC power supply (1 of 3, phase A) in BEEAM AC validation experiments
Mean Well | SE-1000-48 | AC/DC Power Supply | SISO | 120 | 48 | 1000 | Laboratory Characterization | Laboratory Characterization | AC-DC Mean Well SE-1000-48 Power Supply | Power Step |  | Mean-Well-SE-1000-48 | Y | [10 empty] | AC/DC power supply (3 of 3, phase C) in BEEAM AC validation experiments
Murata | D2U5T-H3-5000-380-HU3C | AC/DC Power Supply | SISO | 208 | 380 | 3500 | Datasheet | NA |  |  | 208V | Murata-D2U5T-H3-5000-380-HU3C-208V | Y | 0.85 | 0.89036 | 0.91795 | 0.92989 | 0.93546 | 0.93957 | 0.94169 | 0.94196 | 0.94289 | 0.94302
Murata | D2U5T-H3-5000-380-HU3C | AC/DC Power Supply | SISO | 480 | 380 | 5000 | Datasheet | NA |  |  | 480V | Murata-D2U5T-H3-5000-380-HU3C-480V | Y | 0.88 | 0.9216 | 0.9403 | 0.9478 | 0.9513 | 0.9535 | 0.9546 | 0.9544 | 0.9544 | 0.9535
Murata | D2U5T-H3-7000-54-HU4C | AC/DC Power Supply | SISO | 480 | 54 | 7000 | Datasheet | NA |  |  |  | Murata-D2U5T-H3-7000-54-HU4C | Y | 0.9039 | 0.9422 | 0.9526 | 0.9587 | 0.9602 | 0.9605 | 0.9605 | 0.9596 | 0.9575 | 0.9551
Murata | MVAB120 | AC/DC Power Supply | SISO | 120 | 48 | 120 | Datasheet | NA |  |  |  | Murata-MVAB120 | Y | 0.73609 | 0.84917 | 0.8742 | 0.89071 | 0.89573 | 0.90098 | 0.90223 | 0.90223 | 0.90148 | 0.89998
Murata | MVAC250 | AC/DC Power Supply | SISO | 120 | 48 | 250 | Datasheet | NA |  |  |  | Murata-MVAC250 | Y | 0.82011 | 0.87908 | 0.90415 | 0.9125 | 0.92215 | 0.92622 | 0.92943 | 0.92793 | 0.9275 | 0.92622
Murata | MVAC400 | AC/DC Power Supply | SISO | 120 | 48 | 400 | Datasheet | NA |  |  |  | Murata-MVAC400 | Y | 0.86442 | 0.89888 | 0.91732 | 0.92075 | 0.92266 | 0.92152 | 0.91961 | 0.91783 | 0.91134 | 0.913
Murata | MVAD040 | AC/DC Power Supply | SISO | 120 | 48 | 40 | Datasheet | NA |  |  |  | Murata-MVAD040 | Y | 0.85928 | 0.88467 | 0.89117 | 0.889 | 0.89117 | 0.89551 | 0.89581 | 0.89643 | 0.90077 | 0.89829
Murata | MVAD065 | AC/DC Power Supply | SISO | 120 | 48 | 65 | Datasheet | NA |  |  |  | Murata-MVAD065 | Y | 0.87041 | 0.88987 | 0.89369 | 0.8949 | 0.89551 | 0.89225 | 0.89906 | 0.89551 | 0.89517 | 0.89488
Murata | MVAD160 | AC/DC Power Supply | SISO | 120 | 48 | 160 | Datasheet | NA |  |  |  | Murata-MVAD160 | Y | 0.80686 | 0.87832 | 0.90281 | 0.91179 | 0.91515 | 0.91662 | 0.91625 | 0.91478 | 0.91275 | 0.90981
Netgear | SAL012F1 NA | AC/DC External Power Supply | SISO | 120 | 12 | 12 | Laboratory Characterization | Laboratory Characterization | AC-DC Netgear SAL012F1 NA Power Supply | Power Step |  | Netgear-SAL012F1-NA | Y
Nextek | PHD16-ACDC-DIM-P-24-6 | Multichannel AC/DC Converter | SIMO | 120 | 24 | 1600 | Laboratory Characterization | Laboratory Characterization | AC-DC Nextek PHD16-ACDC-DIM-P-24-6 Multichannel Converter (120V) | Power Step | 120V | Nextek-PHD16-ACDC-DIM-P-24-6-120V | Y
Nextek | PHD16-ACDC-DIM-P-24-6 | Multichannel AC/DC Converter | SIMO | 208 | 24 | 1600 | Laboratory Characterization | Laboratory Characterization | AC-DC Nextek PHD16-ACDC-DIM-P-24-6 Multichannel Converter (208V) | Power Step | 208V | Nextek-PHD16-ACDC-DIM-P-24-6-208V | Y | [10 empty] | PFC; use as representative harmonic spectrum for P > 1000W
Nextek | PHD-Blade-S9 | Multichannel AC/DC Converter | SIMO | 120 | 24 | 1200 | Laboratory Characterization | Laboratory Characterization | AC-DC Nextek PHD-Blade-S9 Multichannel Converter (120V) | Power Step | 120V | Nextek-PHD-Blade-S9-120V | Y
Nextek | PHD-Blade-S9 | Multichannel AC/DC Converter | SIMO | 208 | 24 | 1200 | Laboratory Characterization | Laboratory Characterization | AC-DC Nextek PHD-Blade-S9 Multichannel Converter (208V) | Power Step | 208V | Nextek-PHD-Blade-S9-208V | Y
Nokia | AC-20U | AC/DC USB Charger | SISO | 120 | 5 | 3.75 | Laboratory Characterization | Laboratory Characterization | AC-DC Nokia AC-20U USB Charger | Power Step |  | Nokia-AC-20U | Y
Omron | S8VM-03024 CD | AC/DC Power Supply | SISO | 120 | 24 | 30 | Laboratory Characterization | Laboratory Characterization | AC-DC Omron S8VM-03024 CD Power Supply | Fractional Load (%) |  | Omron-S8VM-03024-CD | Y
Osram | Oti 48/120-277/2A0 DIM 1 AUX G2 | AC/DC LED Driver | SISO | 120 | 12 | 48 | Laboratory Characterization | Laboratory Characterization | AC-DC Osram OTi48 LED Driver | Power Step |  | Osram-Oti-48-120-277-2A0-DIM-1-AUX-G2 | Y
Phillips | Xi040C070V056CnJ1 | AC/DC LED Driver | SISO | 120 | 48 | 40 | Datasheet | NA |  |  | 120V | Phillips-Xi040C070V056CnJ1-120V | Y | 0.57264 | 0.72424 | 0.79245 | 0.8284 | 0.84637 | 0.85742 | 0.86554 | 0.87096 | 0.87312 | 0.87607
Phillips | Xi040C070V056CnJ1 | AC/DC LED Driver | SISO | 277 | 48 | 40 | Datasheet | NA |  |  | 277V | Phillips-Xi040C070V056CnJ1-277V | Y | 0.5499 | 0.70529 | 0.78487 | 0.82602 | 0.85038 | 0.86825 | 0.87962 | 0.88828 | 0.89586 | 0.89965
Phillips | XI075C200V054XPT1 | AC/DC LED Driver | SISO | 120 | 48 | 75 | Datasheet | NA |  |  | 120V | Phillips-XI075C200V054XPT1-120V | Y | 0.65086 | 0.76962 | 0.84042 | 0.85711 | 0.86846 | 0.87581 | 0.87714 | 0.87848 | 0.87647 | 0.87247
Phillips | XI075C200V054XPT1 | AC/DC LED Driver | SISO | 277 | 48 | 75 | Datasheet | NA |  |  | 277V | Phillips-XI075C200V054XPT1-277V | Y | 0.65839 | 0.77959 | 0.84203 | 0.86375 | 0.87889 | 0.89008 | 0.89666 | 0.8993 | 0.90127 | 0.90085
Recom | REDIN120 | AC/DC Power Supply | SISO | 120 | 48 | 120 | Datasheet | NA |  |  |  | Recom-REDIN120 | Y | 0.76107 | 0.84106 | 0.86648 | 0.88081 | 0.88429 | 0.88572 | 0.89022 | 0.89063 | 0.89063 | 0.89071
Recom | REDIN240 | AC/DC Power Supply | SISO | 120 | 48 | 240 | Datasheet | NA |  |  |  | Recom-REDIN240 | Y | 0.74395 | 0.8591 | 0.89093 | 0.90297 | 0.90756 | 0.90972 | 0.9099 | 0.9099 | 0.90891 | 0.90881
Samsung | ETA0U10JBE | AC/DC USB Charger | SISO | 120 | 5 | 3.5 | Laboratory Characterization | Laboratory Characterization | AC-DC Samsung ETA0U10JBE USB Charger (Device 1) | Power Step | 1 | Samsung-ETA0U10JBE-1 | Y | [10 empty] | Use as representative harmonic spectrum for P <= 10W
Samsung | ETA0U10JBE | AC/DC USB Charger | SISO | 120 | 5 | 3.5 | Laboratory Characterization | Laboratory Characterization | AC-DC Samsung ETA0U10JBE USB Charger (Device 2) | Power Step | 2 | Samsung-ETA0U10JBE-2 | N
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 12 | 348 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 12V out, fan off) | Power Step | 12V-Fan-Off | Seasonic-SSR-550PX-12V-Fan-Off | Y | [10 empty] | Each voltage output characterized independently; PFC; use as representative harmonic spectrum for 120W < P <= 1000W
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 12 | 348 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 12V out, fan on) | Power Step | 12V-Fan-On | Seasonic-SSR-550PX-12V-Fan-On | N | [10 empty] | Each voltage output characterized independently
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 3.3 | 66 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 3.3V out, fan off) | Power Step | 3.3V-Fan-Off | Seasonic-SSR-550PX-3.3V-Fan-Off | Y | [10 empty] | Each voltage output characterized independently
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 3.3 | 66 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 3.3V out, fan on) | Power Step | 3.3V-Fan-On | Seasonic-SSR-550PX-3.3V-Fan-On | N | [10 empty] | Each voltage output characterized independently
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 5 | 100 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 5V out, fan off) | Power Step | 5V-Fan-Off | Seasonic-SSR-550PX-5V-Fan-Off | Y | [10 empty] | Each voltage output characterized independently
Seasonic | SSR-550PX | AC/DC Computer Power Supply | SIMO | 120 | 5 | 100 | Laboratory Characterization | Laboratory Characterization | AC-DC Seasonic SSR-550PX Computer Power Supply (120V in, 5V out, fan on) | Power Step | 5V-Fan-On | Seasonic-SSR-550PX-5V-Fan-On | N | [10 empty] | Each voltage output characterized independently
ShenZhen SOY Technology | SUN-0900070 | AC/DC External Power Supply | SISO | 120 | 9 | 6.3 | Laboratory Characterization | Laboratory Characterization | AC-DC ShenZhen SOY Technology SUN-0900070 Power Supply | Power Step |  | ShenZhen-SOY-Technology-SUN-0900070 | Y
SynQor | AQ0300IU48 | AC/DC Power Supply | SISO | 120 | 48 | 300 | Datasheet | NA |  |  |  | SynQor-AQ0300IU48 | Y | 0.76765 | 0.86228 | 0.88622 | 0.89972 | 0.90478 | 0.90635 | 0.90638 | 0.90566 | 0.9037 | 0.89912
SynQor | AQ0400IU48 | AC/DC Power Supply | SISO | 120 | 48 | 400 | Datasheet | NA |  |  |  | SynQor-AQ0400IU48 | Y | 0.80846 | 0.8758 | 0.89644 | 0.90453 | 0.90607 | 0.90568 | 0.90474 | 0.89914 | 0.89298 | 0.88698
SynQor | AQ0500IU48 | AC/DC Power Supply | SISO | 120 | 48 | 500 | Datasheet | NA |  |  |  | SynQor-AQ0500IU48 | Y | 0.8524 | 0.89409 | 0.90507 | 0.90586 | 0.90405 | 0.89645 | 0.88742 | 0.87644 | 0.86624 | 0.85799
SynQor | AQ0800IU48 | AC/DC Power Supply | SISO | 120 | 48 | 800 | Datasheet | NA |  |  |  | SynQor-AQ0800IU48 | Y | 0.83379 | 0.89432 | 0.91223 | 0.92216 | 0.92524 | 0.92515 | 0.92287 | 0.92173 | 0.91869 | 0.91717
SynQor | AQ1100IU48 | AC/DC Power Supply | SISO | 120 | 48 | 1100 | Datasheet | NA |  |  |  | SynQor-AQ1100IU48 | Y | 0.86438 | 0.90709 | 0.92203 | 0.92516 | 0.92525 | 0.92288 | 0.91984 | 0.91605 | 0.91285 | 0.90845
SynQor | AQ1400IU48 | AC/DC Power Supply | SISO | 120 | 48 | 1400 | Datasheet | NA |  |  |  | SynQor-AQ1400IU48 | Y | 0.88848 | 0.91792 | 0.92514 | 0.92286 | 0.91975 | 0.91485 | 0.9088 | 0.90158 | 0.89451 | 0.8879
Tekpower | TP6005E | AC/DC Power Supply | SISO | 120 | 60 | 300 | Laboratory Characterization | Laboratory Characterization | AC-DC Tekpower TP6005E Power Supply | Power Step |  | Tekpower-TP6005E | Y
TPV Electronics | ADPC1945 | AC/DC External Power Supply | SISO | 120 | 19 | 45 | Laboratory Characterization | Laboratory Characterization | AC-DC TPV Electronics ADPC1945 Power Supply | Power Step |  | TPV-Electronics-ADPC1945 | Y
Unknown | US2018 | AC/DC USB Charger | SIMO | 120 | 5 | 10.2 | Laboratory Characterization | Laboratory Characterization | AC-DC (Unknown Manufacturer) US2018 USB Charger (Lower port) | Power Step | Port1 | Unknown-US2018-Port1 | Y | [10 empty] | Each port characterized independently
Unknown | US2018 | AC/DC USB Charger | SIMO | 120 | 5 | 10.2 | Laboratory Characterization | Laboratory Characterization | AC-DC (Unknown Manufacturer) US2018 USB Charger (Upper port) | Power Step | Port2 | Unknown-US2018-Port2 | N | [10 empty] | Each port characterized independently
VeriFone | Au-790Mu | AC/DC External Power Supply | SISO | 120 | 6 | 13.5 | Laboratory Characterization | Laboratory Characterization | AC-DC VeriFone Au-790Mu Power Supply | Power Step |  | VeriFone-Au-790Mu | Y
Vicor | PFM4414xB6M48D0yzz | AC/DC Power Supply | SISO | 120 | 48 | 400 | Datasheet | NA |  |  |  | Vicor-PFM4414xB6M48D0yzz | Y | 0.78209 | 0.86926 | 0.89384 | 0.90752 | 0.91805 | 0.92344 | 0.92613 | 0.92806 | 0.92909 | 0.92997
Vicor | PFM4914xB6M48D0yzz | AC/DC Power Supply | SISO | 120 | 48 | 400 | Datasheet | NA |  |  |  | Vicor-PFM4914xB6M48D0yzz | Y | 0.78021 | 0.86478 | 0.88912 | 0.90298 | 0.91318 | 0.91907 | 0.92169 | 0.92339 | 0.92404 | 0.92483
Wanptek | KPS3010DF | AC/DC Power Supply | SISO | 120 | 30 | 300 | Laboratory Characterization | Laboratory Characterization | AC-DC Wanptek KPS3010DF Power Supply | Power Step |  | Wanptek-KPS3010DF | Y
XPPower | CCB200PS48 | AC/DC Power Supply | SISO | 120 | 48 | 200 | Datasheet | NA |  |  | 120V | XPPower-CCB200PS48-120V | Y | 0.87547 | 0.91334 | 0.92659 | 0.93331 | 0.94079 | 0.94183 | 0.94544 | 0.94467 | 0.94389 | 0.94475
XPPower | CCB200PS48 | AC/DC Power Supply | SISO | 277 | 48 | 200 | Datasheet | NA |  |  | 277V | XPPower-CCB200PS48-277V | Y | 0.87977 | 0.91764 | 0.93089 | 0.93846 | 0.94509 | 0.94698 | 0.94888 | 0.94982 | 0.95077 | 0.95077
XPPower | EMA212PS48 | AC/DC Power Supply | SISO | 120 | 48 | 212 | Datasheet | NA |  |  |  | XPPower-EMA212PS48 | Y | 0.71552 | 0.79418 | 0.83875 | 0.86235 | 0.87021 | 0.87808 | 0.88332 | 0.88857 | 0.89119 | 0.89381
XPPower | EMH350PS48 | AC/DC Power Supply | SISO | 120 | 48 | 350 | Datasheet | NA |  |  | 120V | XPPower-EMH350PS48-120V | Y | 0.6547 | 0.76599 | 0.8209 | 0.83634 | 0.85116 | 0.85993 | 0.86508 | 0.86726 | 0.86775 | 0.87158
XPPower | EMH350PS48 | AC/DC Power Supply | SISO | 277 | 48 | 350 | Datasheet | NA |  |  | 277V | XPPower-EMH350PS48-277V | Y | 0.66025 | 0.76266 | 0.81535 | 0.84301 | 0.86005 | 0.86993 | 0.88063 | 0.88392 | 0.88886 | 0.8938
XPPower | LCL500PS48 | AC/DC Power Supply | SISO | 120 | 48 | 500 | Datasheet | NA |  |  |  | XPPower-LCL500PS48 | Y | 0.76472 | 0.85255 | 0.87958 | 0.88741 | 0.89524 | 0.90147 | 0.9061 | 0.90433 | 0.90577 | 0.9056
XPPower | MHP1000PS48 | AC/DC Power Supply | SISO | 120 | 48 | 1000 | Datasheet | NA |  |  |  | XPPower-MHP1000PS48 | Y | 0.70646 | 0.76798 | 0.7886 | 0.82037 | 0.8303 | 0.83805 | 0.84209 | 0.8447 | 0.84448 | 0.84284
XPPower | MHP650PS48 | AC/DC Power Supply | SISO | 120 | 48 | 600 | Datasheet | NA |  |  |  | XPPower-MHP650PS48 | Y | 0.70769 | 0.76735 | 0.78925 | 0.81971 | 0.83131 | 0.8384 | 0.84266 | 0.84523 | 0.84549 | 0.84381
XPPower | SHP1000PS48 | AC/DC Power Supply | SISO | 120 | 48 | 1000 | Datasheet | NA |  |  |  | XPPower-SHP1000PS48 | Y | 0.73649 | 0.80591 | 0.83283 | 0.84983 | 0.85833 | 0.86541 | 0.86966 | 0.87391 | 0.87533 | 0.87533
XPPower | SHP350PS48 | AC/DC Power Supply | SISO | 120 | 48 | 350 | Datasheet | NA |  |  |  | XPPower-SHP350PS48 | Y | 0.64851 | 0.73573 | 0.75163 | 0.7611 | 0.77477 | 0.78457 | 0.79469 | 0.79706 | 0.80126 | 0.80396
XPPower | SHP650PS48 | AC/DC Power Supply | SISO | 120 | 48 | 650 | Datasheet | NA |  |  |  | XPPower-SHP650PS48 | Y | 0.70832 | 0.76798 | 0.79165 | 0.82179 | 0.83194 | 0.83903 | 0.84328 | 0.84426 | 0.84404 | 0.84404
Xunbuma | T-1000-48 | AC/DC Power Supply | SISO | 120 | 48 | 1000 | Laboratory Characterization | Laboratory Characterization | AC-DC Xunbuma T-1000-48 Power Supply | Power Step |  | Xunbuma-T-1000-48 | Y | [10 empty] | AC/DC power supply (2 of 3, phase B) in BEEAM AC validation experiments
Zmoon | A1749 | AC/DC Laptop Power Supply | SISO | 120 | 15 | 90 | Laboratory Characterization | Laboratory Characterization | AC-DC Zmoon A1749 Laptop Power Supply | Power Step |  | Zmoon-A1749 | Y
Note on O1: Data from tables or plots in manufacturers' data sheets. Graphical plot data digitized using WebPlotDigitizer (https://automeris.io/WebPlotDigitizer/)
Note on D2: SISO = Single-input, single-output SIMO = Single-input, multi-output MISO = Multi-input, single-output MIMO = Multi-input, multi-output
Note on E2: If rated voltage is a range, set to the voltage that corresponds to the characterization data.
Note on F2: If rated voltage is a range, set to the voltage that corresponds to the characterization data. If multiple, set to the largest absolute value.
Note on G2: For multi-output devices, this is the total power for all outputs
Note on N2: This column is set to "N" (no) for laboratory characterization device data sets that are largely redundant with another data set. Multiple instances of the same device under the same voltage conditions were eliminated, but multiple instances of the same device under different voltage conditions were retained.

## DC-DC Converters
Device Metadata |  |  |  | Device Ratings |  |  | Characterization Metadata |  | Output Configuration |  |  | Efficiency Curve Data | [9 empty] | Other
Manufacturer | Model | Description | Type | Rated Voltage Input (V) | Rated Voltage Output (V) | Rated Power Output (W) | Efficiency Data Source | Data Directory | Disambiguation Suffix | Model Label | Use? | Eff @ 10% | Eff @ 20% | Eff @ 30% | Eff @ 40% | Eff @ 50% | Eff @ 60% | Eff @ 70% | Eff @ 80% | Eff @ 90% | Eff @ 100% | Notes | Issues
Apollo | T80HV | MPPT Charge Controller | SISO | 43 | 48 | 5120 | Datasheet |  |  | Apollo-T80HV | Y | 0.98709 | 0.99036 | 0.99005 | 0.98892 | 0.98737 | 0.98572 | 0.9839 | 0.98207 | 0.98022 | 0.97826
Bixpower | BX-DD90X | Laptop Power Supply | SISO | 24 | 18.5 | 90 | Laboratory Characterization | DC-DC Bixpower BX-DD90X Laptop Power Supply (Device 1) | 1 | Bixpower-BX-DD90X-1 | Y | [10 empty] | DC/DC laptop power supply (1 of 3) in BEEAM DC validation experiments
Bixpower | BX-DD90X | Laptop Power Supply | SISO | 24 | 18.5 | 90 | Laboratory Characterization | DC-DC Bixpower BX-DD90X Laptop Power Supply (Device 2) | 2 | Bixpower-BX-DD90X-2 | N | [10 empty] | DC/DC laptop power supply (2 of 3) in BEEAM DC validation experiments
Bixpower | BX-DD90X | Laptop Power Supply | SISO | 24 | 18.5 | 90 | Laboratory Characterization | DC-DC Bixpower BX-DD90X Laptop Power Supply (Device 3) | 3 | Bixpower-BX-DD90X-3 | N | [10 empty] | DC/DC laptop power supply (3 of 3) in BEEAM DC validation experiments
Bixpower | BX-DD90X | Laptop Power Supply | SISO | 24 | 15 | 90 | Laboratory Characterization | DC-DC Bixpower BX-DD90X Laptop Power Supply (Device 4) | 4 | Bixpower-BX-DD90X-4 | Y | [10 empty] | Device has variable output; this one tested at 15V
Bixpower | BX-DD90X | Laptop Power Supply | SISO | 12 | 19.5 | 90 | Laboratory Characterization | DC-DC Bixpower BX-DD90X Laptop Power Supply (Device 5) | 5 | Bixpower-BX-DD90X-5 | Y
Emerson | C 400/48-3500e | DC/DC Converter | SISO | 380 | 48 | 3500 | Datasheet |  |  | Emerson-C-400-48-3500e | Y | 0.94803 | 0.96146 | 0.96522 | 0.96764 | 0.96845 | 0.96818 | 0.96683 | 0.96468 | 0.96307 | 0.96039
Emerson | S48-2000e3 | DC/DC Converter | SISO | 380 | 48 | 2000 | Datasheet |  |  | Emerson-S48-2000e3 | Y | 0.89091 | 0.94361 | 0.95758 | 0.96195 | 0.96457 | 0.9642 | 0.96422 | 0.96246 | 0.96137 | 0.95904
Gearmo | GM-UCPDCARB | Automotive USB Adapter | SISO | 12 | 5 | 15 | Laboratory Characterization | DC-DC Gearmo GM-UCPDCARB Automotive USB Adapter (12VDC) | 12V | Gearmo-GM-UCPDCARB-12V | Y
Gearmo | GM-UCPDCARB | Automotive USB Adapter | SISO | 24 | 5 | 15 | Laboratory Characterization | DC-DC Gearmo GM-UCPDCARB Automotive USB Adapter (24VDC) | 24V | Gearmo-GM-UCPDCARB-24V | Y
HP | F1455A | Laptop Power Supply | SISO | 12 | 19 | 75 | Laboratory Characterization | DC-DC HP F1455A Laptop Power Supply |  | HP-F1455A | Y
IEI Technology | ACE-4520C | DC/DC Power Supply | SISO | 24 | 12 | 120 | Laboratory Characterization | DC-DC IEI Technology ACE-4520C Computer Power Supply |  | IEI-Technology-ACE-4520C | Y
Integrated Power Designs | DC2-110-4006-CHCO | DC/DC Power Supply | SIMO | 24 | 24 | 110 | Laboratory Characterization | DC-DC Integrated Power Designs DC2-110-4006-CHCO Power Supply |  | Integrated-Power-Designs-DC2-110-4006-CHCO | Y | [10 empty] | 5V, 12V, 24V
Integrated Power Designs | DC2-185-4001-CH | DC/DC Power Supply | SIMO | 24 | 12 | 185 | Laboratory Characterization | DC-DC Integrated Power Designs DC2-185-4001-CH Power Supply |  | Integrated-Power-Designs-DC2-185-4001-CH | Y | [10 empty] | 3.3V, 5V, 12V
Integrated Power Designs | DC2-70-4006-CHCO | DC/DC Power Supply | SIMO | 24 | 24 | 70 | Laboratory Characterization | DC-DC Integrated Power Designs DC2-70-4006-CHCO Power Supply |  | Integrated-Power-Designs-DC2-70-4006-CHCO | Y | [10 empty] | 5V, 12V, 24V
Integrated Power Designs | DC4-110-4006-CHCO | DC/DC Power Supply | SIMO | 48 | 24 | 110 | Laboratory Characterization | DC-DC Integrated Power Designs DC4-110-4006-CHCO Power Supply |  | Integrated-Power-Designs-DC4-110-4006-CHCO | Y | [10 empty] | 5V, 12V, 24V
Integrated Power Designs | DC4-70-4006-CHCO | DC/DC Power Supply | SIMO | 48 | 24 | 70 | Laboratory Characterization | DC-DC Integrated Power Designs DC4-70-4006-CHCO Power Supply |  | Integrated-Power-Designs-DC4-70-4006-CHCO | Y | [10 empty] | 5V, 12V, 24V
Linear | LT3590 | DC/DC LED Driver | SISO | 48 | 12 | 3 | Datasheet |  |  | Linear-LT3590 | Y | 0.52637 | 0.86584 | 0.87918 | 0.89327 | 0.89845 | 0.9029 | 0.9029 | 0.9029 | 0.9029 | 0.90512
Linear | LT3763 | DC/DC LED Driver | SISO | 48 | 12 | 240 | Datasheet |  |  | Linear-LT3763 | Y | 0.91038 | 0.93235 | 0.95358 | 0.95976 | 0.96346 | 0.96519 | 0.96519 | 0.96445 | 0.96272 | 0.96074
Mean Well | RSD-30G-12 | DC/DC Power Supply | SISO | 12 | 12 | 30 | Laboratory Characterization | DC-DC Mean Well RSD-30G-12 Power Supply (12VDC) | 12V | Mean-Well-RSD-30G-12-12V | Y | [10 empty] | Characterized at both 12V and 24V input
Mean Well | RSD-30G-12 | DC/DC Power Supply | SISO | 24 | 12 | 30 | Laboratory Characterization | DC-DC Mean Well RSD-30G-12 Power Supply (24VDC) | 24V | Mean-Well-RSD-30G-12-24V | Y | [10 empty] | Characterized at both 12V and 24V input
Mean Well | RSD-30G-24 | DC/DC Power Supply | SISO | 12 | 24 | 30 | Laboratory Characterization | DC-DC Mean Well RSD-30G-24 Power Supply (12VDC) | 12V | Mean-Well-RSD-30G-24-12V | Y | [10 empty] | Characterized at both 12V and 24V input
Mean Well | RSD-30G-24 | DC/DC Power Supply | SISO | 24 | 24 | 30 | Laboratory Characterization | DC-DC Mean Well RSD-30G-24 Power Supply (24VDC) | 24V | Mean-Well-RSD-30G-24-24V | Y | [10 empty] | Characterized at both 12V and 24V input
Mean Well | SD-100A-24 | DC/DC Power Supply | SISO | 12 | 24 | 100 | Laboratory Characterization | DC-DC Mean Well SD-100A-24 Power Supply |  | Mean-Well-SD-100A-24 | Y
Mean Well | SD-100B-12 | DC/DC Power Supply | SISO | 24 | 12 | 100 | Laboratory Characterization | DC-DC Mean Well SD-100B-12 Power Supply |  | Mean-Well-SD-100B-12 | Y
Morningstar | TS-MPPT-30 | MPPT Charge Controller | SISO | 52 | 48 | 1600 | Datasheet |  |  | Morningstar-TS-MPPT-30 | Y | 0.98582 | 0.98896 | 0.99059 | 0.99109 | 0.99159 | 0.99184 | 0.99159 | 0.99134 | 0.99097 | 0.99046
Morningstar | TS-MPPT-45 | MPPT Charge Controller | SISO | 52 | 48 | 2400 | Datasheet |  |  | Morningstar-TS-MPPT-45 | Y | 0.98582 | 0.98896 | 0.99059 | 0.99109 | 0.99159 | 0.99184 | 0.99159 | 0.99134 | 0.99097 | 0.99046
Morningstar | TS-MPPT-60 | MPPT Charge Controller | SISO | 52 | 48 | 3200 | Datasheet |  |  | Morningstar-TS-MPPT-60 | Y | 0.98582 | 0.98896 | 0.99059 | 0.99109 | 0.99159 | 0.99184 | 0.99159 | 0.99134 | 0.99097 | 0.99046
Morningstar | TS-MPPT-60-600V | MPPT Charge Controller | SISO | 300 | 48 | 3200 | Datasheet |  |  | Morningstar-TS-MPPT-60-600V | Y | 0.92832 | 0.95775 | 0.96762 | 0.97264 | 0.97351 | 0.97801 | 0.97697 | 0.97489 | 0.9734 | 0.97197
Nextek | 1600-C2-Z-380 | Multichannel DC/DC Converter | SIMO | 380 | 24 | 1600 | Laboratory Characterization | DC-DC Nextek 1600-C2-Z-380 Multichannel Converter (380VDC) |  | Nextek-1600-C2-Z-380 | Y | [10 empty] | Unit installed at the Alliance Center in Denver, CO
Nextek | PHD16-ACDC-DIM-P-24-6 | Multichannel DC/DC Converter | SIMO | 380 | 24 | 1600 | Laboratory Characterization | DC-DC Nextek PHD16-ACDC-DIM-P-24-6 Multichannel Converter (380VDC) |  | Nextek-PHD16-ACDC-DIM-P-24-6 | Y | [10 empty] | Central AC/DC converter in BEEAM DC validation experiments
Nextek | PHD-Blade-S9 | Multichannel DC/DC Converter | SIMO | 380 | 24 | 1200 | Laboratory Characterization | DC-DC Nextek PHD-Blade-S9 Multichannel Converter (380VDC) |  | Nextek-PHD-Blade-S9 | Y
Outback | Flexmax 60 | MPPT Charge Controller | SISO | 68 | 48 | 3000 | Datasheet |  |  | Outback-Flexmax-60 | Y | 0.96707 | 0.98012 | 0.98156 | 0.9806 | 0.9788 | 0.97641 | 0.97377 | 0.97102 | 0.96826 | 0.96539
Outback | Flexmax 80 | MPPT Charge Controller | SISO | 68 | 48 | 4000 | Datasheet |  |  | Outback-Flexmax-80 | Y | 0.96707 | 0.98012 | 0.98156 | 0.9806 | 0.9788 | 0.97641 | 0.97377 | 0.97102 | 0.96826 | 0.96539
Outtage | PA-4900-OT | Laptop Power Supply | SISO | 12 | 19 | 90 | Laboratory Characterization | DC-DC Outtage PA-4900-OT Power Supply |  | Outtage-PA-4900-OT | Y
Powerseed | PA-3900-Z3 | Laptop Power Supply | SISO | 12 | 19 | 90 | Laboratory Characterization | DC-DC Powerseed PA-3900-Z3 Power Supply |  | Powerseed-PA-3900-Z3 | Y
SolarEdge | P300 | DC Power Optimizer | SISO | 35 | 48 | 300 | Datasheet |  |  | SolarEdge-P300 | Y | 0.97178 | 0.98631 | 0.99136 | 0.99386 | 0.99499 | 0.99515 | 0.99471 | 0.99407 | 0.99407 | 0.99295
SolarEdge | P400 | DC Power Optimizer | SISO | 50 | 48 | 400 | Datasheet |  |  | SolarEdge-P400 | Y | 0.97043 | 0.98578 | 0.99046 | 0.99251 | 0.99326 | 0.99326 | 0.99326 | 0.99326 | 0.99289 | 0.99251
SolarEdge | P600 | DC Power Optimizer | SISO | 60 | 48 | 600 | Datasheet |  |  | SolarEdge-P600 | Y | 0.96747 | 0.98413 | 0.98958 | 0.99157 | 0.99255 | 0.99255 | 0.99255 | 0.99255 | 0.99216 | 0.99249
SolarEdge | P700 | DC Power Optimizer | SISO | 80 | 48 | 700 | Datasheet |  |  | SolarEdge-P700 | Y | 0.97847 | 0.98456 | 0.98944 | 0.99036 | 0.99091 | 0.99111 | 0.99188 | 0.99269 | 0.99237 | 0.99278
SynQor | BQ4H480FTx64 | DC/DC Converter | SISO | 380 | 48 | 3040 | Datasheet |  |  | SynQor-BQ4H480FTx64 | Y | 0.97096 | 0.97589 | 0.97778 | 0.97875 | 0.97857 | 0.97828 | 0.97747 | 0.97647 | 0.97567 | 0.97482
SynQor | IQ4H480FTX13 | DC/DC Converter | SISO | 380 | 48 | 600 | Datasheet |  |  | SynQor-IQ4H480FTX13 | Y | 0.83447 | 0.88981 | 0.90728 | 0.91408 | 0.91602 | 0.91602 | 0.91553 | 0.91311 | 0.91262 | 0.91311
SynQor | IQ4H480HTX06 | DC/DC Converter | SISO | 380 | 48 | 300 | Datasheet |  |  | SynQor-IQ4H480HTX06 | Y | 0.62204 | 0.76311 | 0.82184 | 0.85146 | 0.86796 | 0.87718 | 0.88301 | 0.88592 | 0.88641 | 0.88641
SynQor | IQ4H480QTx03 | DC/DC Converter | SISO | 380 | 48 | 156 | Datasheet |  |  | SynQor-IQ4H480QTx03 | Y | 0.63264 | 0.77062 | 0.82623 | 0.85592 | 0.87097 | 0.88101 | 0.88477 | 0.88686 | 0.88603 | 0.88394
SynQor | MCOTS-C-270-48-FT | DC/DC Converter | SISO | 380 | 48 | 600 | Datasheet |  |  | SynQor-MCOTS-C-270-48-FT | Y | 0.82906 | 0.88501 | 0.90347 | 0.9107 | 0.91335 | 0.91322 | 0.91275 | 0.91105 | 0.91041 | 0.91088
SynQor | MCOTS-C-270-48-QT | DC/DC Converter | SISO | 380 | 48 | 150 | Datasheet |  |  | SynQor-MCOTS-C-270-48-QT | Y | 0.60041 | 0.73184 | 0.79571 | 0.83263 | 0.84876 | 0.86157 | 0.86777 | 0.87231 | 0.87231 | 0.87231
Unknown | CRA-HLY-PD65W | Automotive USB Adapter | SISO | 12 | 5 | 15 | Laboratory Characterization | DC-DC (Unknown Manufacturer) CRA-HLY-PD65W Automotive USB Adapter (12VDC) | 12V | Unknown-CRA-HLY-PD65W-12V | Y | [10 empty] | Characterized at both 12V and 24V input
Unknown | CRA-HLY-PD65W | Automotive USB Adapter | SISO | 24 | 5 | 15 | Laboratory Characterization | DC-DC (Unknown Manufacturer) CRA-HLY-PD65W Automotive USB Adapter (24VDC) | 24V | Unknown-CRA-HLY-PD65W-24V | Y | [10 empty] | Characterized at both 12V and 24V input
Unknown | USB-Adapter-Generic | Automotive USB Adapter | SISO | 12 | 5 | 10.5 | Laboratory Characterization | DC-DC (Unknown Manufacturer) Generic Automotive USB Adapter (12VDC, bottom port) | A-12V | Unknown-USB-Adapter-Generic-A-12V | Y | [10 empty] | Each port characterized independently at both 12V and 24V input
Unknown | USB-Adapter-Generic | Automotive USB Adapter | SISO | 24 | 5 | 10.5 | Laboratory Characterization | DC-DC (Unknown Manufacturer) Generic Automotive USB Adapter (24VDC, bottom port) | A-24V | Unknown-USB-Adapter-Generic-A-24V | Y | [10 empty] | Each port characterized independently at both 12V and 24V input
Unknown | USB-Adapter-Generic | Automotive USB Adapter | SISO | 12 | 5 | 10.5 | Laboratory Characterization | DC-DC (Unknown Manufacturer) Generic Automotive USB Adapter (12VDC, top port) | B-12V | Unknown-USB-Adapter-Generic-B-12V | N | [10 empty] | Each port characterized independently at both 12V and 24V input
Unknown | USB-Adapter-Generic | Automotive USB Adapter | SISO | 24 | 5 | 10.5 | Laboratory Characterization | DC-DC (Unknown Manufacturer) Generic Automotive USB Adapter (24VDC, top port) | B-24V | Unknown-USB-Adapter-Generic-B-24V | N | [10 empty] | Each port characterized independently at both 12V and 24V input
Verizon | MIC34DUALVPC-F2 | Automotive USB Adapter | SISO | 12 | 5 | 17 | Laboratory Characterization | DC-DC Verizon MIC34DUALVPC-F2 (12VDC, micro-USB port) | 12V-MicroUSB | Verizon-MIC34DUALVPC-F2-12V-MicroUSB | Y | [10 empty] | Each port characterized independently at both 12V and 24V input
Verizon | MIC34DUALVPC-F2 | Automotive USB Adapter | SISO | 12 | 5 | 17 | Laboratory Characterization | DC-DC Verizon MIC34DUALVPC-F2 (12VDC, standard USB port) | 12V-USBA | Verizon-MIC34DUALVPC-F2-12V-USBA | N | [10 empty] | Each port characterized independently at both 12V and 24V input
Verizon | MIC34DUALVPC-F2 | Automotive USB Adapter | SISO | 24 | 5 | 17 | Laboratory Characterization | DC-DC Verizon MIC34DUALVPC-F2 (24VDC, micro-USB port) | 24V-MicroUSB | Verizon-MIC34DUALVPC-F2-24V-MicroUSB | Y | [10 empty] | Each port characterized independently at both 12V and 24V input
Verizon | MIC34DUALVPC-F2 | Automotive USB Adapter | SISO | 24 | 5 | 17 | Laboratory Characterization | DC-DC Verizon MIC34DUALVPC-F2 (24VDC, standard USB port) | 24V-USBA | Verizon-MIC34DUALVPC-F2-24V-USBA | N | [10 empty] | Each port characterized independently at both 12V and 24V input
Vicor | BCM384x480y325Bzz | DC/DC Converter | SISO | 380 | 48 | 325 | Datasheet |  |  | Vicor-BCM384x480y325Bzz | Y | 0.83554 | 0.90434 | 0.93142 | 0.94495 | 0.95195 | 0.95675 | 0.95937 | 0.96069 | 0.96157 | 0.962
Vicor | BCM6123xD0G5030yzz | DC/DC Converter | SISO | 380 | 48 | 1500 | Datasheet |  |  | Vicor-BCM6123xD0G5030yzz | Y | 0.94842 | 0.97063 | 0.9768 | 0.97858 | 0.97889 | 0.97801 | 0.97655 | 0.9751 | 0.97306 | 0.97103
Vicor | BCM6123xD1E5117yzz | DC/DC Converter | SISO | 380 | 48 | 867 | Datasheet |  |  | Vicor-BCM6123xD1E5117yzz | Y | 0.90956 | 0.95027 | 0.96395 | 0.97052 | 0.97367 | 0.97422 | 0.97527 | 0.97526 | 0.97474 | 0.97421
Vicor | BCM6123xD1E5126yzz | DC/DC Converter | SISO | 380 | 48 | 1318 | Datasheet |  |  | Vicor-BCM6123xD1E5126yzz | Y | 0.93861 | 0.96471 | 0.97329 | 0.97697 | 0.9782 | 0.97854 | 0.97818 | 0.97763 | 0.97657 | 0.9755
Vicor | BCM6123xD1E5135yzz | DC/DC Converter | SISO | 380 | 48 | 1796 | Datasheet |  |  | Vicor-BCM6123xD1E5135yzz | Y | 0.94462 | 0.96831 | 0.97545 | 0.97809 | 0.9785 | 0.97823 | 0.97704 | 0.97546 | 0.97374 | 0.97189
Note on M1: Data from tables or plots in manufacturers' data sheets. Graphical plot data digitized using WebPlotDigitizer (https://automeris.io/WebPlotDigitizer/)
Note on D2: SISO = Single-input, single-output SIMO = Single-input, multi-output MISO = Multi-input, single-output MIMO = Multi-input, multi-output
Note on E2: If rated voltage is a range, set to the voltage that corresponds to the characterization data.
Note on F2: If rated voltage is a range, set to the voltage that corresponds to the characterization data. If multiple, set to the largest absolute value.
Note on G2: For multi-output devices, this is the total power for all outputs
Note on L2: This column is set to "N" (no) for laboratory characterization device data sets that are largely redundant with another data set. Multiple instances of the same device under the same voltage conditions were eliminated, but multiple instances of the same device under different voltage conditions were retained.

## PV Inverters
Device Metadata |  |  | Device Ratings |  |  |  |  | Characterization Metadata | Output Configuration |  |  | Efficiency Curve Data | [24 empty] | Other
Manufacturer | Model | Description | Minimum Voltage Input (V) | Rated Voltage Input (V) | Maximum Voltage Input (V) | Rated Voltage Output (V) | Rated Power Output (kW) | Efficiency Data Source | Disambiguation Suffix | Model Label | Use? | Night Tare Loss (W) | Power Level 10% (kW) | Power Level 20% (kW) | Power Level 30% (kW) | Power Level 50% (kW) | Power Level 75% (kW) | Power Level 100% (kW) | Efficiency @ Vmin 10% (%) | Efficiency @ Vmin 20% (%) | Efficiency @ Vmin 30% (%) | Efficiency @ Vmin 50% (%) | Efficiency @ Vmin 75% (%) | Efficiency @ Vmin 100% (%) | Efficiency @ Vnom 10% (%) | Efficiency @ Vnom 20% (%) | Efficiency @ Vnom 30% (%) | Efficiency @ Vnom 50% (%) | Efficiency @ Vnom 75% (%) | Efficiency @ Vnom 100% (%) | Efficiency @ Vmax 10% (%) | Efficiency @ Vmax 20% (%) | Efficiency @ Vmax 30% (%) | Efficiency @ Vmax 50% (%) | Efficiency @ Vmax 75% (%) | Efficiency @ Vmax 100% (%) | Notes | Issues
ABB | PVI-3.0-OUTD-S-US-A | PV Inverter | 100 | 310 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-PVI-3.0-OUTD-S-US-A-208V | Y | 0.1 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5
ABB | PVI-3.0-OUTD-S-US-A | PV Inverter | 100 | 340 | 480 | 240 | 3 | CEC Inverter Database | 240V | ABB-PVI-3.0-OUTD-S-US-A-240V | Y | 0.1 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2
ABB | PVI-3.0-OUTD-S-US-A | PV Inverter | 100 | 390 | 480 | 277 | 3 | CEC Inverter Database | 277V | ABB-PVI-3.0-OUTD-S-US-A-277V | Y | 0.2 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7
ABB | PVI-3.0-OUTD-S-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-PVI-3.0-OUTD-S-US-Z-A-208V | Y | 0.1 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5
ABB | PVI-3.0-OUTD-S-US-Z-A | PV Inverter | 100 | 340 | 480 | 240 | 3 | CEC Inverter Database | 240V | ABB-PVI-3.0-OUTD-S-US-Z-A-240V | Y | 0.1 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2
ABB | PVI-3.0-OUTD-S-US-Z-A | PV Inverter | 100 | 390 | 480 | 277 | 3 | CEC Inverter Database | 277V | ABB-PVI-3.0-OUTD-S-US-Z-A-277V | Y | 0.2 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7
ABB | PVI-3.0-OUTD-S-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-PVI-3.0-OUTD-S-US-Z-M-A-208V | Y | 0.1 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5
ABB | PVI-3.0-OUTD-S-US-Z-M-A | PV Inverter | 100 | 340 | 480 | 240 | 3 | CEC Inverter Database | 240V | ABB-PVI-3.0-OUTD-S-US-Z-M-A-240V | Y | 0.1 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2
ABB | PVI-3.0-OUTD-S-US-Z-M-A | PV Inverter | 100 | 390 | 480 | 277 | 3 | CEC Inverter Database | 277V | ABB-PVI-3.0-OUTD-S-US-Z-M-A-277V | Y | 0.2 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA | PV Inverter | 200 | 340 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.3-TL-PLUS-US-SB-RA-208V | Y | 0.9 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 340 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.3-TL-PLUS-US-SB-RA-Q-208V | Y | 0.9 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA | PV Inverter | 200 | 340 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.3-TL-PLUS-US-SE-RA-208V | Y | 0.9 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 340 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.3-TL-PLUS-US-SZM-RA-208V | Y | 0.9 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 340 | 480 | 208 | 3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.3-TL-PLUS-US-SZ-RA-208V | Y | 0.9 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.3 | CEC Inverter Database | 240V | ABB-UNO-DM-3.3-TL-PLUS-US-SB-RA-240V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 355 | 480 | 240 | 3.3 | CEC Inverter Database | 240V | ABB-UNO-DM-3.3-TL-PLUS-US-SB-RA-Q-240V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.3 | CEC Inverter Database | 240V | ABB-UNO-DM-3.3-TL-PLUS-US-SE-RA-240V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.3 | CEC Inverter Database | 240V | ABB-UNO-DM-3.3-TL-PLUS-US-SZM-RA-240V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.3 | CEC Inverter Database | 240V | ABB-UNO-DM-3.3-TL-PLUS-US-SZ-RA-240V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA | PV Inverter | 200 | 340 | 480 | 208 | 3.3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.8-TL-PLUS-US-SB-RA-208V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 340 | 480 | 208 | 3.3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.8-TL-PLUS-US-SB-RA-Q-208V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA | PV Inverter | 200 | 340 | 480 | 208 | 3.3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.8-TL-PLUS-US-SE-RA-208V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 340 | 480 | 208 | 3.3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.8-TL-PLUS-US-SZM-RA-208V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 340 | 480 | 208 | 3.3 | CEC Inverter Database | 208V | ABB-UNO-DM-3.8-TL-PLUS-US-SZ-RA-208V | Y | 0.9 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96
ABB | PVI-3.6-OUTD-S-US-A | PV Inverter | 100 | 310 | 480 | 208 | 3.6 | CEC Inverter Database | 208V | ABB-PVI-3.6-OUTD-S-US-A-208V | Y | 0.1 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7
ABB | PVI-3.6-OUTD-S-US-A | PV Inverter | 100 | 340 | 480 | 240 | 3.6 | CEC Inverter Database | 240V | ABB-PVI-3.6-OUTD-S-US-A-240V | Y | 0.2 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3
ABB | PVI-3.6-OUTD-S-US-A | PV Inverter | 100 | 395 | 480 | 277 | 3.6 | CEC Inverter Database | 277V | ABB-PVI-3.6-OUTD-S-US-A-277V | Y | 0.2 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8
ABB | PVI-3.6-OUTD-S-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 3.6 | CEC Inverter Database | 208V | ABB-PVI-3.6-OUTD-S-US-Z-A-208V | Y | 0.1 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7
ABB | PVI-3.6-OUTD-S-US-Z-A | PV Inverter | 100 | 340 | 480 | 240 | 3.6 | CEC Inverter Database | 240V | ABB-PVI-3.6-OUTD-S-US-Z-A-240V | Y | 0.2 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3
ABB | PVI-3.6-OUTD-S-US-Z-A | PV Inverter | 100 | 395 | 480 | 277 | 3.6 | CEC Inverter Database | 277V | ABB-PVI-3.6-OUTD-S-US-Z-A-277V | Y | 0.2 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8
ABB | PVI-3.6-OUTD-S-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 3.6 | CEC Inverter Database | 208V | ABB-PVI-3.6-OUTD-S-US-Z-M-A-208V | Y | 0.1 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7
ABB | PVI-3.6-OUTD-S-US-Z-M-A | PV Inverter | 100 | 340 | 480 | 240 | 3.6 | CEC Inverter Database | 240V | ABB-PVI-3.6-OUTD-S-US-Z-M-A-240V | Y | 0.2 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3
ABB | PVI-3.6-OUTD-S-US-Z-M-A | PV Inverter | 100 | 395 | 480 | 277 | 3.6 | CEC Inverter Database | 277V | ABB-PVI-3.6-OUTD-S-US-Z-M-A-277V | Y | 0.2 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8
ABB | PVI-3.8-OUTD-S-US-A | PV Inverter | 100 | 310 | 480 | 208 | 3.8 | CEC Inverter Database | 208V | ABB-PVI-3.8-OUTD-S-US-A-208V | Y | 0.12 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8
ABB | PVI-3.8-OUTD-S-US-A | PV Inverter | 100 | 340 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-PVI-3.8-OUTD-S-US-A-240V | Y | 0.16 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3
ABB | PVI-3.8-OUTD-S-US-A | PV Inverter | 100 | 395 | 480 | 277 | 3.8 | CEC Inverter Database | 277V | ABB-PVI-3.8-OUTD-S-US-A-277V | Y | 0.22 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8
ABB | PVI-3.8-OUTD-S-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 3.8 | CEC Inverter Database | 208V | ABB-PVI-3.8-OUTD-S-US-Z-A-208V | Y | 0.12 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8
ABB | PVI-3.8-OUTD-S-US-Z-A | PV Inverter | 100 | 340 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-PVI-3.8-OUTD-S-US-Z-A-240V | Y | 0.16 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3
ABB | PVI-3.8-OUTD-S-US-Z-A | PV Inverter | 100 | 395 | 480 | 277 | 3.8 | CEC Inverter Database | 277V | ABB-PVI-3.8-OUTD-S-US-Z-A-277V | Y | 0.22 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8
ABB | PVI-3.8-OUTD-S-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 3.8 | CEC Inverter Database | 208V | ABB-PVI-3.8-OUTD-S-US-Z-M-A-208V | Y | 0.12 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8
ABB | PVI-3.8-OUTD-S-US-Z-M-A | PV Inverter | 100 | 340 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-PVI-3.8-OUTD-S-US-Z-M-A-240V | Y | 0.16 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3
ABB | PVI-3.8-OUTD-S-US-Z-M-A | PV Inverter | 100 | 395 | 480 | 277 | 3.8 | CEC Inverter Database | 277V | ABB-PVI-3.8-OUTD-S-US-Z-M-A-277V | Y | 0.22 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-UNO-DM-3.8-TL-PLUS-US-SB-RA-240V | Y | 1 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 355 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-UNO-DM-3.8-TL-PLUS-US-SB-RA-Q-240V | Y | 1 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-UNO-DM-3.8-TL-PLUS-US-SE-RA-240V | Y | 1 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-UNO-DM-3.8-TL-PLUS-US-SZM-RA-240V | Y | 1 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 355 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | ABB-UNO-DM-3.8-TL-PLUS-US-SZ-RA-240V | Y | 1 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5
ABB | PVI-4.2-OUTD-S-US-A | PV Inverter | 100 | 310 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-PVI-4.2-OUTD-S-US-A-208V | Y | 0.1 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5
ABB | PVI-4.2-OUTD-S-US-A | PV Inverter | 100 | 340 | 480 | 240 | 4.2 | CEC Inverter Database | 240V | ABB-PVI-4.2-OUTD-S-US-A-240V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2
ABB | PVI-4.2-OUTD-S-US-A | PV Inverter | 100 | 395 | 480 | 277 | 4.2 | CEC Inverter Database | 277V | ABB-PVI-4.2-OUTD-S-US-A-277V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7
ABB | PVI-4.2-OUTD-S-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-PVI-4.2-OUTD-S-US-Z-A-208V | Y | 0.1 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5
ABB | PVI-4.2-OUTD-S-US-Z-A | PV Inverter | 100 | 340 | 480 | 240 | 4.2 | CEC Inverter Database | 240V | ABB-PVI-4.2-OUTD-S-US-Z-A-240V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2
ABB | PVI-4.2-OUTD-S-US-Z-A | PV Inverter | 100 | 395 | 480 | 277 | 4.2 | CEC Inverter Database | 277V | ABB-PVI-4.2-OUTD-S-US-Z-A-277V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7
ABB | PVI-4.2-OUTD-S-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-PVI-4.2-OUTD-S-US-Z-M-A-208V | Y | 0.1 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5
ABB | PVI-4.2-OUTD-S-US-Z-M-A | PV Inverter | 100 | 340 | 480 | 240 | 4.2 | CEC Inverter Database | 240V | ABB-PVI-4.2-OUTD-S-US-Z-M-A-240V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2
ABB | PVI-4.2-OUTD-S-US-Z-M-A | PV Inverter | 100 | 395 | 480 | 277 | 4.2 | CEC Inverter Database | 277V | ABB-PVI-4.2-OUTD-S-US-Z-M-A-277V | Y | 0.2 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA | PV Inverter | 200 | 340 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-UNO-DM-4.6-TL-PLUS-US-SB-RA-208V | Y | 0.9 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 340 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-UNO-DM-4.6-TL-PLUS-US-SB-RA-Q-208V | Y | 0.9 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA | PV Inverter | 200 | 340 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-UNO-DM-4.6-TL-PLUS-US-SE-RA-208V | Y | 0.9 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 340 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-UNO-DM-4.6-TL-PLUS-US-SZM-RA-208V | Y | 0.9 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 340 | 480 | 208 | 4.2 | CEC Inverter Database | 208V | ABB-UNO-DM-4.6-TL-PLUS-US-SZ-RA-208V | Y | 0.9 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA | PV Inverter | 200 | 355 | 480 | 240 | 4.6 | CEC Inverter Database | 240V | ABB-UNO-DM-4.6-TL-PLUS-US-SB-RA-240V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA-Q | PV Inverter | 200 | 355 | 480 | 240 | 4.6 | CEC Inverter Database | 240V | ABB-UNO-DM-4.6-TL-PLUS-US-SB-RA-Q-240V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA | PV Inverter | 200 | 355 | 480 | 240 | 4.6 | CEC Inverter Database | 240V | ABB-UNO-DM-4.6-TL-PLUS-US-SE-RA-240V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 355 | 480 | 240 | 4.6 | CEC Inverter Database | 240V | ABB-UNO-DM-4.6-TL-PLUS-US-SZM-RA-240V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 355 | 480 | 240 | 4.6 | CEC Inverter Database | 240V | ABB-UNO-DM-4.6-TL-PLUS-US-SZ-RA-240V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SB-RA-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA-QU | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SB-RA-QU-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SE-RA-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SZM-RA-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SZ-RA-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA-U | PV Inverter | 240 | 340 | 480 | 208 | 4.6 | CEC Inverter Database | 208V | ABB-UNO-DM-5.0-TL-PLUS-US-SZ-RA-U-208V | Y | 1 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3
ABB | PVI-5000-OUTD-US-A | PV Inverter | 100 | 310 | 480 | 208 | 5 | CEC Inverter Database | 208V | ABB-PVI-5000-OUTD-US-A-208V | Y | 0.18 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | PVI-5000-OUTD-US-A | PV Inverter | 100 | 345 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-PVI-5000-OUTD-US-A-240V | Y | 0.24 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3
ABB | PVI-5000-OUTD-US-A | PV Inverter | 100 | 400 | 480 | 277 | 5 | CEC Inverter Database | 277V | ABB-PVI-5000-OUTD-US-A-277V | Y | 0.32 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9
ABB | PVI-5000-OUTD-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 5 | CEC Inverter Database | 208V | ABB-PVI-5000-OUTD-US-Z-A-208V | Y | 0.18 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | PVI-5000-OUTD-US-Z-A | PV Inverter | 100 | 345 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-PVI-5000-OUTD-US-Z-A-240V | Y | 0.24 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3
ABB | PVI-5000-OUTD-US-Z-A | PV Inverter | 100 | 400 | 480 | 277 | 5 | CEC Inverter Database | 277V | ABB-PVI-5000-OUTD-US-Z-A-277V | Y | 0.32 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9
ABB | PVI-5000-OUTD-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 5 | CEC Inverter Database | 208V | ABB-PVI-5000-OUTD-US-Z-M-A-208V | Y | 0.18 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9
ABB | PVI-5000-OUTD-US-Z-M-A | PV Inverter | 100 | 345 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-PVI-5000-OUTD-US-Z-M-A-240V | Y | 0.24 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3
ABB | PVI-5000-OUTD-US-Z-M-A | PV Inverter | 100 | 400 | 480 | 277 | 5 | CEC Inverter Database | 277V | ABB-PVI-5000-OUTD-US-Z-M-A-277V | Y | 0.32 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SB-RA-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA-QU | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SB-RA-QU-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SE-RA-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SZM-RA-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SZ-RA-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA-U | PV Inverter | 200 | 355 | 480 | 240 | 5 | CEC Inverter Database | 240V | ABB-UNO-DM-5.0-TL-PLUS-US-SZ-RA-U-240V | Y | 1 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8
ABB | PVI-6000-OUTD-US-A | PV Inverter | 100 | 310 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-PVI-6000-OUTD-US-A-208V | Y | 0.18 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7
ABB | PVI-6000-OUTD-US-A | PV Inverter | 100 | 345 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-PVI-6000-OUTD-US-A-240V | Y | 0.24 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2
ABB | PVI-6000-OUTD-US-A | PV Inverter | 100 | 400 | 480 | 277 | 6 | CEC Inverter Database | 277V | ABB-PVI-6000-OUTD-US-A-277V | Y | 0.32 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9
ABB | PVI-6000-OUTD-US-Z-A | PV Inverter | 100 | 310 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-PVI-6000-OUTD-US-Z-A-208V | Y | 0.18 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7
ABB | PVI-6000-OUTD-US-Z-A | PV Inverter | 100 | 345 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-PVI-6000-OUTD-US-Z-A-240V | Y | 0.24 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2
ABB | PVI-6000-OUTD-US-Z-A | PV Inverter | 100 | 400 | 480 | 277 | 6 | CEC Inverter Database | 277V | ABB-PVI-6000-OUTD-US-Z-A-277V | Y | 0.32 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9
ABB | PVI-6000-OUTD-US-Z-M-A | PV Inverter | 100 | 310 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-PVI-6000-OUTD-US-Z-M-A-208V | Y | 0.18 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7
ABB | PVI-6000-OUTD-US-Z-M-A | PV Inverter | 100 | 345 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-PVI-6000-OUTD-US-Z-M-A-240V | Y | 0.24 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2
ABB | PVI-6000-OUTD-US-Z-M-A | PV Inverter | 100 | 400 | 480 | 277 | 6 | CEC Inverter Database | 277V | ABB-PVI-6000-OUTD-US-Z-M-A-277V | Y | 0.32 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-SB-RA-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-SB-RA-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA-QU | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-SB-RA-QU-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA-QU | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-SB-RA-QU-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-SC-RA-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-SC-RA-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-SE-RA-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-SE-RA-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-S-XRA-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-S-XRA-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA | PV Inverter | 240 | 340 | 480 | 208 | 6 | CEC Inverter Database | 208V | ABB-UNO-DM-6.0-TL-PLUS-US-SZM-RA-208V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA | PV Inverter | 200 | 355 | 480 | 240 | 6 | CEC Inverter Database | 240V | ABB-UNO-DM-6.0-TL-PLUS-US-SZM-RA-240V | Y | 1.3 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4
ABB | UNO-7.6-TL-OUTD-S-US-A | PV Inverter | 200 | 340 | 480 | 208 | 7.6 | CEC Inverter Database | 208V | ABB-UNO-7.6-TL-OUTD-S-US-A-208V | Y | 1.3 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7
ABB | UNO-7.6-TL-OUTD-S-US-A | PV Inverter | 200 | 380 | 480 | 240 | 7.6 | CEC Inverter Database | 240V | ABB-UNO-7.6-TL-OUTD-S-US-A-240V | Y | 1.4 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2
ABB | UNO-7.6-TL-OUTD-S-US-A | PV Inverter | 200 | 380 | 480 | 277 | 7.6 | CEC Inverter Database | 277V | ABB-UNO-7.6-TL-OUTD-S-US-A-277V | Y | 1.5 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7
ABB | UNO-7.6-TL-OUTD-S-US-Z-A | PV Inverter | 200 | 340 | 480 | 208 | 7.6 | CEC Inverter Database | 208V | ABB-UNO-7.6-TL-OUTD-S-US-Z-A-208V | Y | 1.3 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7
ABB | UNO-7.6-TL-OUTD-S-US-Z-A | PV Inverter | 200 | 380 | 480 | 240 | 7.6 | CEC Inverter Database | 240V | ABB-UNO-7.6-TL-OUTD-S-US-Z-A-240V | Y | 1.4 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2
ABB | UNO-7.6-TL-OUTD-S-US-Z-A | PV Inverter | 200 | 380 | 480 | 277 | 7.6 | CEC Inverter Database | 277V | ABB-UNO-7.6-TL-OUTD-S-US-Z-A-277V | Y | 1.5 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A | PV Inverter | 200 | 340 | 480 | 208 | 7.6 | CEC Inverter Database | 208V | ABB-UNO-7.6-TL-OUTD-S-US-Z-M-A-208V | Y | 1.3 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A | PV Inverter | 200 | 380 | 480 | 240 | 7.6 | CEC Inverter Database | 240V | ABB-UNO-7.6-TL-OUTD-S-US-Z-M-A-240V | Y | 1.4 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A | PV Inverter | 200 | 380 | 480 | 277 | 7.6 | CEC Inverter Database | 277V | ABB-UNO-7.6-TL-OUTD-S-US-Z-M-A-277V | Y | 1.5 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7
ABB | UNO-8.6-TL-OUTD-S-US-A | PV Inverter | 200 | 380 | 480 | 240 | 8.6 | CEC Inverter Database | 240V | ABB-UNO-8.6-TL-OUTD-S-US-A-240V | Y | 1.4 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2
ABB | UNO-8.6-TL-OUTD-S-US-A | PV Inverter | 200 | 380 | 480 | 277 | 8.6 | CEC Inverter Database | 277V | ABB-UNO-8.6-TL-OUTD-S-US-A-277V | Y | 1.5 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6
ABB | UNO-8.6-TL-OUTD-S-US-Z-A | PV Inverter | 200 | 380 | 480 | 240 | 8.6 | CEC Inverter Database | 240V | ABB-UNO-8.6-TL-OUTD-S-US-Z-A-240V | Y | 1.4 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2
ABB | UNO-8.6-TL-OUTD-S-US-Z-A | PV Inverter | 200 | 380 | 480 | 277 | 8.6 | CEC Inverter Database | 277V | ABB-UNO-8.6-TL-OUTD-S-US-Z-A-277V | Y | 1.5 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A | PV Inverter | 200 | 380 | 480 | 240 | 8.6 | CEC Inverter Database | 240V | ABB-UNO-8.6-TL-OUTD-S-US-Z-M-A-240V | Y | 1.4 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A | PV Inverter | 200 | 380 | 480 | 277 | 8.6 | CEC Inverter Database | 277V | ABB-UNO-8.6-TL-OUTD-S-US-Z-M-A-277V | Y | 1.5 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6
ABB | TRIO-50.0-TL-OUTD-US-480 | PV Inverter | 520 | 720 | 800 | 480 | 50 | CEC Inverter Database | 480V | ABB-TRIO-50.0-TL-OUTD-US-480-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 96.3426 | 97.3941 | 97.7305 | 97.8494 | 97.8642 | 97.7358 | 96.859 | 98.0033 | 98.3351 | 98.526 | 98.5515 | 98.4933 | 95.9226 | 97.5683 | 98.0341 | 98.3179 | 98.3432 | 98.3043
ABB | TRIO-60.0-TL-OUTD-US-480 | PV Inverter | 570 | 720 | 800 | 480 | 60 | CEC Inverter Database | 480V | ABB-TRIO-60.0-TL-OUTD-US-480-480V | Y | 0.8 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.7 | 97.9 | 98 | 98 | 97.8 | 97.2 | 98.1 | 98.4 | 98.5 | 98.5 | 98.4 | 96.4 | 97.8 | 98.1 | 98.3 | 98.3 | 98.2
ABB | TRIO-TM-60.0-US-480 | PV Inverter | 570 | 720 | 800 | 480 | 60 | CEC Inverter Database | 480V | ABB-TRIO-TM-60.0-US-480-480V | Y | 0.6 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.6 | 97.8 | 97.9 | 97.8 | 97.6 | 97.3 | 98.3 | 98.5 | 98.6 | 98.6 | 98.4 | 96.7 | 98 | 98.3 | 98.4 | 98.4 | 98.3
ABB | PVS-60-TL-R-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-R-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-60-TL-SC-R-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-SC-R-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-60-TL-SC-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-SC-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-60-TL-S-R-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-S-R-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-60-TL-S-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-S-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-60-TL-US | PV Inverter | 570 | 720 | 800 | 480 | 60.033 | CEC Inverter Database | 480V | ABB-PVS-60-TL-US-480V | Y | 0.9 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517
ABB | PVS-166-TL-POWER-MODULE-1-US | PV Inverter | 850 | 1100 | 1200 | 800 | 165.954 | CEC Inverter Database | 800V | ABB-PVS-166-TL-POWER-MODULE-1-US-800V | Y | 12 | 16.595 | 33.191 | 49.786 | 82.977 | 124.466 | 165.954 | 96.77 | 98.03 | 98.27 | 98.39 | 98.32 | 98.15 | 96.7 | 98.08 | 98.39 | 98.53 | 98.48 | 98.34 | 95.77 | 97.71 | 98.11 | 98.23 | 98.33 | 98.25
ABB | PVS-166-TL-POWER-MODULE-2-US | PV Inverter | 850 | 1100 | 1200 | 800 | 165.954 | CEC Inverter Database | 800V | ABB-PVS-166-TL-POWER-MODULE-2-US-800V | Y | 12 | 16.595 | 33.191 | 49.786 | 82.977 | 124.466 | 165.954 | 96.77 | 98.03 | 98.27 | 98.39 | 98.32 | 98.15 | 96.7 | 98.08 | 98.39 | 98.53 | 98.48 | 98.34 | 95.77 | 97.71 | 98.11 | 98.23 | 98.33 | 98.25
ABB | PVS-175-TL-POWER-MODULE-1-US | PV Inverter | 850 | 1100 | 1200 | 800 | 179.574 | CEC Inverter Database | 800V | ABB-PVS-175-TL-POWER-MODULE-1-US-800V | Y | 12 | 17.957 | 35.915 | 53.872 | 89.787 | 134.681 | 179.574 | 95.65 | 97.31 | 97.7 | 97.83 | 97.59 | 97.24 | 95.6 | 97.4 | 97.8 | 97.94 | 97.76 | 97.52 | 94.83 | 97.05 | 97.53 | 97.62 | 97.61 | 97.36
ABB | PVS-175-TL-POWER-MODULE-2-US | PV Inverter | 850 | 1100 | 1200 | 800 | 179.574 | CEC Inverter Database | 800V | ABB-PVS-175-TL-POWER-MODULE-2-US-800V | Y | 12 | 17.957 | 35.915 | 53.872 | 89.787 | 134.681 | 179.574 | 95.65 | 97.31 | 97.7 | 97.83 | 97.59 | 97.24 | 95.6 | 97.4 | 97.8 | 97.94 | 97.76 | 97.52 | 94.83 | 97.05 | 97.53 | 97.62 | 97.61 | 97.36
Altenergy Power System Inc. | YC600 | PV Inverter | 24 | 36 | 45 | 240 | 0.55 | CEC Inverter Database | 240V | Altenergy-Power-System-Inc.-YC600-240V | Y | 0.02 | 0.0548 | 0.1096 | 0.1644 | 0.274 | 0.411 | 0.548 | 94.4 | 95.9 | 96 | 96.4 | 96.3 | 96.1 | 94.1 | 95.8 | 96.2 | 96.5 | 96.7 | 96.6 | 93.7 | 95.7 | 95.8 | 96.4 | 96.7 | 96.7
Altenergy Power System Inc. | QS1 | PV Inverter | 27 | 37.5 | 48 | 208 | 1.2183 | CEC Inverter Database | 208V | Altenergy-Power-System-Inc.-QS1-208V | Y | 0.046 | 0.12183 | 0.24366 | 0.36549 | 0.60914 | 0.91372 | 1.2183 | 95.4629 | 96.4508 | 96.5764 | 96.5697 | 96.1392 | 95.4927 | 95.1509 | 96.3907 | 96.7164 | 96.7168 | 96.3775 | 95.9339 | 94.854 | 96.1629 | 96.0576 | 96.5787 | 96.3787 | 95.9939
Altenergy Power System Inc. | QS1 | PV Inverter | 27 | 37.5 | 48 | 240 | 1.225 | CEC Inverter Database | 240V | Altenergy-Power-System-Inc.-QS1-240V | Y | 0.09 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942
Altenergy Power System Inc. | QS1200 | PV Inverter | 27 | 37.5 | 48 | 240 | 1.225 | CEC Inverter Database | 240V | Altenergy-Power-System-Inc.-QS1200-240V | Y | 0.09 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942
Altenergy Power System Inc. | QS1A | PV Inverter | 30 | 41 | 52 | 240 | 1.516 | CEC Inverter Database | 240V | Altenergy-Power-System-Inc.-QS1A-240V | Y | 0.038 | 0.152 | 0.303 | 0.455 | 0.758 | 1.137 | 1.516 | 95.51 | 96.54 | 96.63 | 96.65 | 96.14 | 95.39 | 95.29 | 96.49 | 96.46 | 96.74 | 96.36 | 95.82 | 94.75 | 96.22 | 96.1 | 96.61 | 96.35 | 95.99
Apparent Inc. | SG424U CA, 120VAC, 60Hz | PV Inverter | 31.2 | 36.4 | 48.9 | 120 | 0.25 | CEC Inverter Database | 120V | Apparent-Inc.-SG424U-CA,-120VAC,-60Hz-120V | Y | 0.45 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 85.4 | 91.1 | 91.5 | 92.1 | 91.8 | 90.6 | 87 | 90.8 | 91.5 | 92.4 | 92.2 | 91.2 | 86.1 | 90.9 | 92 | 92.2 | 92.4 | 92
Canadian Solar Inc. | CSI-25K-T480GL01-UB | PV Inverter | 347 | 470 | 800 | 480 | 24.958 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-25K-T480GL01-UB-480V | Y | 1 | 2.4958 | 4.9916 | 7.4874 | 12.479 | 18.7185 | 24.9581 | 97.8538 | 98.3868 | 98.42 | 98.5665 | 98.4105 | 98.354 | 98.0001 | 98.4275 | 98.4174 | 98.6659 | 98.423 | 98.3476 | 97.893 | 98.4187 | 98.493 | 98.685 | 98.4659 | 98.373
Canadian Solar Inc. | CSI-25KTL-GS-FL | PV Inverter | 580 | 650 | 780 | 480 | 25 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-25KTL-GS-FL-480V | Y | 14 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5
Canadian Solar Inc. | CSI-25KTL-GS-FLB | PV Inverter | 580 | 650 | 770 | 480 | 25 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-25KTL-GS-FLB-480V | Y | 14 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.143 | 97.3103 | 97.5582 | 97.902 | 98.1863 | 97.7856 | 97.1369 | 97.2947 | 97.4013 | 97.8837 | 98.2954 | 97.7509 | 97.2361 | 97.396 | 97.5435 | 97.6922 | 98.0012 | 97.4855
Canadian Solar Inc. | CSI-30K-T480GL01-UB | PV Inverter | 417 | 700 | 800 | 480 | 29.948 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-30K-T480GL01-UB-480V | Y | 1 | 2.9948 | 5.9895 | 8.9843 | 14.9738 | 22.4607 | 29.9477 | 97.7689 | 98.392 | 98.4344 | 98.5669 | 98.4121 | 98.3166 | 97.814 | 98.4242 | 98.504 | 98.651 | 98.42 | 98.356 | 97.89 | 98.4279 | 98.517 | 98.6982 | 98.451 | 98.365
Canadian Solar Inc. | CSI-30KTL-GS-FL | PV Inverter | 580 | 650 | 780 | 480 | 30 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-30KTL-GS-FL-480V | Y | 15 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8
Canadian Solar Inc. | CSI-30KTL-GS-FLB | PV Inverter | 580 | 650 | 780 | 480 | 30 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-30KTL-GS-FLB-480V | Y | 15 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1367 | 97.9124 | 97.905 | 98.3089 | 97.8705 | 97.9174 | 97.3783 | 98.0388 | 98.0359 | 98.3477 | 98.1139 | 97.915 | 97.12 | 97.8656 | 97.9617 | 98.2389 | 97.9687 | 97.8103
Canadian Solar Inc. | CSI-36K-T480GL01-UB | PV Inverter | 500 | 700 | 800 | 480 | 35.925 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-36K-T480GL01-UB-480V | Y | 1 | 3.5925 | 7.185 | 10.7775 | 17.9625 | 26.9438 | 35.9251 | 97.7435 | 98.365 | 98.4061 | 98.579 | 98.4309 | 98.3073 | 97.796 | 98.3474 | 98.465 | 98.636 | 98.468 | 98.334 | 97.826 | 98.4038 | 98.496 | 98.6621 | 98.483 | 98.319
Canadian Solar Inc. | CSI-36KTL-CT | PV Inverter | 540 | 730 | 800 | 480 | 36 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-36KTL-CT-480V | Y | 0 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2
Canadian Solar Inc. | CSI-36KTL-GS-FL | PV Inverter | 580 | 650 | 780 | 480 | 36 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-36KTL-GS-FL-480V | Y | 15 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1
Canadian Solar Inc. | CSI-36KTL-GS-FLB | PV Inverter | 580 | 650 | 780 | 480 | 36 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-36KTL-GS-FLB-480V | Y | 15 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3556 | 98.1469 | 98.1132 | 98.3457 | 98.0215 | 98.1483 | 97.6545 | 98.3164 | 98.2591 | 98.438 | 98.343 | 98.1379 | 97.3624 | 98.154 | 98.2138 | 98.3749 | 98.1715 | 98.0758
Canadian Solar Inc. | CSI-40K-T480GL01-UB | PV Inverter | 556 | 700 | 800 | 480 | 39.926 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-40K-T480GL01-UB-480V | Y | 1 | 3.9926 | 7.9852 | 11.9778 | 19.9629 | 29.9444 | 39.9259 | 97.7566 | 98.3499 | 98.431 | 98.5651 | 98.4319 | 98.3273 | 97.787 | 98.3669 | 98.459 | 98.628 | 98.441 | 98.347 | 97.832 | 98.4148 | 98.466 | 98.635 | 98.515 | 98.336
Canadian Solar Inc. | CSI-40KTL-GS | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-40KTL-GS-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98
Canadian Solar Inc. | CSI-40KTL-GS-B | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-40KTL-GS-B-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.47 | 98.0068 | 98.0574 | 98.1972 | 98.114 | 98.0292 | 97.9259 | 98.3089 | 98.392 | 98.7145 | 98.5725 | 98.3423 | 97.5823 | 98.1565 | 98.1932 | 98.4353 | 98.3489 | 98.2444
Canadian Solar Inc. | CSI-40KTL-GS-FL | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-40KTL-GS-FL-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2
Canadian Solar Inc. | CSI-40KTL-GS-FLB | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-40KTL-GS-FLB-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.4777 | 98.0039 | 98.0564 | 98.1952 | 98.1258 | 98.0274 | 97.9247 | 98.3105 | 98.4002 | 98.7211 | 98.5785 | 98.342 | 97.5764 | 98.1504 | 98.1795 | 98.4337 | 98.3428 | 98.244
Canadian Solar Inc. | CSI-50K-T480GL01-UB | PV Inverter | 568 | 720 | 850 | 480 | 49.916 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50K-T480GL01-UB-480V | Y | 1 | 4.9916 | 9.9832 | 14.9748 | 24.9581 | 37.4371 | 49.9161 | 97.752 | 98.3642 | 98.434 | 98.585 | 98.42 | 98.313 | 97.791 | 98.3809 | 98.447 | 98.645 | 98.443 | 98.352 | 97.84 | 98.411 | 98.483 | 98.68 | 98.493 | 98.3201
Canadian Solar Inc. | CSI-50KTL-CT | PV Inverter | 480 | 730 | 850 | 480 | 50 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50KTL-CT-480V | Y | 0.88 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6089 | 96.843 | 97.4816 | 97.8549 | 97.8327 | 97.6904 | 98.0184 | 98.6275 | 98.7749 | 98.8023 | 98.7196 | 98.6108 | 97.7339 | 98.4586 | 98.6223 | 98.6594 | 98.5869 | 98.4698
Canadian Solar Inc. | CSI-50KTL-GS | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50KTL-GS-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7 | 98.4 | 98.5 | 98.6 | 98.5 | 98.4 | 97.8 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 97.9 | 98.6 | 98.7 | 98.8 | 98.6 | 98.5
Canadian Solar Inc. | CSI-50KTL-GS-B | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50KTL-GS-B-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644
Canadian Solar Inc. | CSI-50KTL-GS-FL | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50KTL-GS-FL-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5
Canadian Solar Inc. | CSI-50KTL-GS-FLB | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-50KTL-GS-FLB-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006
Canadian Solar Inc. | CSI-60K-T480GL01-UB | PV Inverter | 526 | 720 | 850 | 480 | 59.933 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-60K-T480GL01-UB-480V | Y | 1 | 5.9933 | 11.9866 | 17.9798 | 29.9664 | 44.9496 | 59.9328 | 97.739 | 98.411 | 98.444 | 98.579 | 98.412 | 98.28 | 97.787 | 98.4024 | 98.465 | 98.622 | 98.441 | 98.342 | 97.809 | 98.434 | 98.522 | 98.689 | 98.48 | 98.326
Canadian Solar Inc. | CSI-60KTL-CT | PV Inverter | 540 | 730 | 850 | 480 | 60 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-60KTL-CT-480V | Y | 0.88 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5104 | 97.4761 | 97.8852 | 98.0525 | 97.9434 | 97.7271 | 98.2227 | 98.7116 | 98.7911 | 98.779 | 98.6548 | 98.4981 | 98.0008 | 98.5506 | 98.6633 | 98.6588 | 98.5228 | 98.3541
Canadian Solar Inc. | CSI-60KTL-GS | PV Inverter | 580 | 650 | 720 | 480 | 60 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-60KTL-GS-480V | Y | 1 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.3 | 98.4 | 98.6 | 98.4 | 98.2 | 97.8 | 98.5 | 98.5 | 98.6 | 98.5 | 98.3 | 97.9 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5
Canadian Solar Inc. | CSI-60KTL-GS-B | PV Inverter | 580 | 650 | 720 | 480 | 60 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-60KTL-GS-B-480V | Y | 1 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499
Canadian Solar Inc. | CSI-66K-T480GL01-UB | PV Inverter | 579 | 720 | 850 | 480 | 65.926 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-66K-T480GL01-UB-480V | Y | 1 | 6.5926 | 13.1851 | 19.7777 | 32.9628 | 49.4441 | 65.9255 | 97.752 | 98.351 | 98.413 | 98.588 | 98.42 | 98.31 | 97.773 | 98.343 | 98.48 | 98.677 | 98.436 | 98.319 | 97.807 | 98.369 | 98.501 | 98.657 | 98.487 | 98.321
Canadian Solar Inc. | CSI-66KTL-GS | PV Inverter | 580 | 650 | 720 | 480 | 66 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-66KTL-GS-480V | Y | 1 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.6 | 98.4 | 98.5 | 98.6 | 98.4 | 98.3 | 97.7 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 97.8 | 98.7 | 98.7 | 98.8 | 98.6 | 98.5
Canadian Solar Inc. | CSI-66KTL-GS-B | PV Inverter | 580 | 650 | 720 | 480 | 66 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-66KTL-GS-B-480V | Y | 1 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918
Canadian Solar Inc. | CSI-75K-T480GL02-U | PV Inverter | 550 | 720 | 850 | 480 | 75 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-75K-T480GL02-U-480V | Y | 1 | 7.5002 | 15.0005 | 22.5007 | 37.5012 | 56.2517 | 75.0023 | 98.147 | 98.5383 | 98.525 | 98.6238 | 98.3792 | 98.2162 | 98.1775 | 98.5215 | 98.5439 | 98.6666 | 98.4445 | 98.2384 | 98.244 | 98.5737 | 99.0148 | 98.6211 | 98.5743 | 98.294
Canadian Solar Inc. | CSI-80K-T480GL02-U | PV Inverter | 550 | 720 | 850 | 480 | 80 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-80K-T480GL02-U-480V | Y | 1 | 8.0003 | 16.0006 | 24.0009 | 40.0015 | 60.0023 | 80.0031 | 98.1441 | 98.5363 | 98.5241 | 98.6265 | 98.3794 | 98.2123 | 98.1764 | 98.5232 | 98.543 | 98.6654 | 98.4447 | 98.2424 | 98.2451 | 98.5776 | 99.0149 | 98.6271 | 98.575 | 98.2898
Canadian Solar Inc. | CSI-90K-T480GL02-U | PV Inverter | 550 | 720 | 850 | 480 | 90 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-90K-T480GL02-U-480V | Y | 1 | 9.0005 | 18.001 | 27.0015 | 45.0024 | 67.5036 | 90.0049 | 98.1425 | 98.5301 | 98.5175 | 98.6202 | 98.382 | 98.2129 | 98.1677 | 98.5208 | 98.5367 | 98.6571 | 98.4429 | 98.2296 | 98.24 | 98.5713 | 99.0158 | 98.6197 | 98.5715 | 98.2914
Canadian Solar Inc. | CSI-100K-T480GL02-U | PV Inverter | 550 | 720 | 850 | 480 | 100 | CEC Inverter Database | 480V | Canadian-Solar-Inc.-CSI-100K-T480GL02-U-480V | Y | 1 | 10.0004 | 20.0008 | 30.0012 | 50.002 | 75.003 | 100.004 | 98.1406 | 98.5261 | 98.5197 | 98.6189 | 98.3796 | 98.2109 | 98.1693 | 98.5244 | 98.5388 | 98.6582 | 98.442 | 98.2301 | 98.242 | 98.5714 | 99.0139 | 98.6188 | 98.571 | 98.2889
Canadian Solar Inc. | CSI-125KTL-GS-E | PV Inverter | 860 | 950 | 1250 | 600 | 125 | CEC Inverter Database | 600V | Canadian-Solar-Inc.-CSI-125KTL-GS-E-600V | Y | 1 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.9167 | 99.0279 | 98.941 | 98.9462 | 98.8521 | 98.7464 | 98.5469 | 98.8405 | 98.7722 | 98.8039 | 98.6338 | 98.6288 | 98.2805 | 98.7 | 98.7947 | 98.6619 | 98.4679 | 98.3006
Canadian Solar Inc. | CSI-125K-T600GL02-U | PV Inverter | 860 | 1080 | 1250 | 600 | 125.083 | CEC Inverter Database | 600V | Canadian-Solar-Inc.-CSI-125K-T600GL02-U-600V | Y | 1 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.2442 | 98.6339 | 98.622 | 98.725 | 98.4773 | 98.3136 | 98.2735 | 98.6299 | 98.6462 | 98.7609 | 98.5469 | 98.336 | 98.3436 | 98.6734 | 99.1159 | 98.7211 | 98.6759 | 98.3966
Canadian Solar Inc. | CSI-185K-T600GL02-U | PV Inverter | 850 | 1080 | 1300 | 600 | 185.005 | CEC Inverter Database | 600V | Canadian-Solar-Inc.-CSI-185K-T600GL02-U-600V | Y | 1 | 18.5005 | 37.0011 | 55.5016 | 92.5026 | 138.7539 | 185.0053 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 97.932 | 98.566 | 98.654 | 98.582 | 98.404 | 98.181 | 97.65 | 98.488 | 98.579 | 98.893 | 98.698 | 98.444
Canadian Solar Inc. | CSI-255K-T800GL02-U | PV Inverter | 850 | 1080 | 1300 | 800 | 255.013 | CEC Inverter Database | 800V | Canadian-Solar-Inc.-CSI-255K-T800GL02-U-800V | Y | 1 | 25.5013 | 51.0025 | 76.5038 | 127.5063 | 191.2595 | 255.0126 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 97.645 | 98.299 | 98.495 | 98.546 | 98.427 | 98.255 | 98.059 | 98.701 | 98.84 | 98.835 | 98.696 | 98.521
CE+T Energy Solutions Inc. | 30C3 | PV Inverter | 550 | 700 | 850 | 480 | 29.99 | CEC Inverter Database | 480V | CE+T-Energy-Solutions-Inc.-30C3-480V | Y | 56.8 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 | PV Inverter | 28 | 30 | 32 | 208 | 0.277 | CEC Inverter Database | 208V | Chilicon-Power,-LLC-CP-250E-60-72-208-240-MC4-208V | Y | 0.02 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 92 | 95.1 | 95.9 | 96 | 95.6 | 94.9 | 91.2 | 94.8 | 95.7 | 96 | 95.6 | 95.1 | 90.6 | 94.5 | 95.6 | 96 | 95.7 | 95.2
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 | PV Inverter | 28 | 30 | 32 | 240 | 0.289 | CEC Inverter Database | 240V | Chilicon-Power,-LLC-CP-250E-60-72-208-240-MC4-240V | Y | 0.06 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.3 | 95.4 | 96.1 | 96.2 | 95.9 | 95.2 | 91.6 | 95.2 | 96 | 96.3 | 96 | 95.4 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.6
Chilicon Power, LLC | CP-720-60/72/96-208/240-MC4 | PV Inverter | 60 | 65 | 70 | 240 | 0.721 | CEC Inverter Database | 240V | Chilicon-Power,-LLC-CP-720-60-72-96-208-240-MC4-240V | Y | 0.1 | 0.072122 | 0.14424 | 0.21637 | 0.36061 | 0.54091 | 0.72122 | 93.1325 | 95.8508 | 96.485 | 96.6636 | 96.3127 | 95.4342 | 92.5062 | 95.5354 | 96.3479 | 96.6951 | 96.2594 | 95.3978 | 91.7173 | 95.2191 | 96.1457 | 96.6114 | 96.0277 | 95.1854
Chilicon Power, LLC | CP-720-60/72/96-208/240-MC4 | PV Inverter | 60 | 65 | 70 | 208 | 0.725 | CEC Inverter Database | 208V | Chilicon-Power,-LLC-CP-720-60-72-96-208-240-MC4-208V | Y | 0.1 | 0.072543 | 0.14509 | 0.21763 | 0.36272 | 0.54407 | 0.72543 | 93.0721 | 95.576 | 96.2371 | 96.3244 | 95.6753 | 94.8437 | 93.0023 | 95.3597 | 96.086 | 96.3359 | 95.7304 | 94.9137 | 92.3998 | 94.8703 | 95.8744 | 96.2342 | 95.6885 | 94.6211
Chint Power Systems America | CPS SCA20KTL-DO-R/US-480 | PV Inverter | 560 | 735 | 850 | 480 | 20 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-SCA20KTL-DO-R-US-480-480V | Y | 3 | 2.0112 | 4.0224 | 6.0336 | 10.056 | 15.0839 | 20.1119 | 96.9815 | 97.6652 | 97.8012 | 97.8313 | 97.6023 | 97.256 | 97.9016 | 98.3305 | 98.4819 | 98.4139 | 98.2956 | 98.149 | 97.5397 | 98.2151 | 98.3121 | 98.2684 | 98.1987 | 97.9889
Chint Power Systems America | CPS SCA25KTL-DO-R/US-480 | PV Inverter | 560 | 735 | 850 | 480 | 25 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-SCA25KTL-DO-R-US-480-480V | Y | 3 | 2.5259 | 5.0517 | 7.5776 | 12.6294 | 18.944 | 25.2587 | 96.9119 | 97.6982 | 97.8295 | 97.8399 | 97.5971 | 97.2868 | 97.8973 | 98.3256 | 98.4773 | 98.4082 | 98.2817 | 98.0946 | 97.5003 | 98.1562 | 98.3137 | 98.2793 | 98.1854 | 97.9963
Chint Power Systems America | CPS SCA25KTL-DO/US-208 | PV Inverter | 480 | 575 | 850 | 208 | 25.432 | CEC Inverter Database | 208V | Chint-Power-Systems-America-CPS-SCA25KTL-DO-US-208-208V | Y | 2.9 | 2.5432 | 5.0864 | 7.6296 | 12.716 | 19.074 | 25.432 | 95.687 | 96.8055 | 97.0311 | 97.0424 | 96.7769 | 96.4735 | 95.3071 | 96.2843 | 96.7871 | 96.7814 | 96.4829 | 96.1186 | 93.5943 | 95.6171 | 96.1229 | 96.3357 | 96.1514 | 95.85
Chint Power Systems America | CPS SCA36KTL-DO/US | PV Inverter | 540 | 730 | 800 | 480 | 36 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-SCA36KTL-DO-US-480V | Y | 0 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2
Chint Power Systems America | CPS SCA50KTL-DO/US-480 | PV Inverter | 480 | 730 | 850 | 480 | 50 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-SCA50KTL-DO-US-480-480V | Y | 0.88 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5
Chint Power Systems America | CPS SCA60KTL-DO/US-480 | PV Inverter | 540 | 730 | 850 | 480 | 60 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-SCA60KTL-DO-US-480-480V | Y | 0.88 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4
Chint Power Systems America | CPS SCH100KTL-AIO/US-600 | PV Inverter | 870 | 1000 | 1300 | 600 | 100 | CEC Inverter Database | 600V | Chint-Power-Systems-America-CPS-SCH100KTL-AIO-US-600-600V | Y | 0.33 | 10.056 | 20.112 | 30.168 | 50.28 | 75.42 | 100.56 | 98.51 | 99 | 99.01 | 99.09 | 98.94 | 98.78 | 98.03 | 98.44 | 98.61 | 98.6 | 98.48 | 98.29 | 97.25 | 97.82 | 98.17 | 98.19 | 98.14 | 97.93
Chint Power Systems America | CPS SCH100KTL-DO/US-600 | PV Inverter | 870 | 1000 | 1300 | 600 | 100 | CEC Inverter Database | 600V | Chint-Power-Systems-America-CPS-SCH100KTL-DO-US-600-600V | Y | 4.5 | 10 | 20 | 30 | 50 | 75 | 100 | 98.5519 | 98.9972 | 99.062 | 99.0008 | 98.8738 | 98.7452 | 97.9026 | 98.4849 | 98.5322 | 98.5674 | 98.447 | 98.2811 | 97.098 | 97.901 | 98.071 | 98.1053 | 98.08 | 97.9054
Chint Power Systems America | CPS SCH125KTL-AIO/US-600 | PV Inverter | 870 | 1000 | 1300 | 600 | 125 | CEC Inverter Database | 600V | Chint-Power-Systems-America-CPS-SCH125KTL-AIO-US-600-600V | Y | 0.33 | 12.555 | 25.109 | 37.664 | 62.773 | 94.16 | 125.546 | 98.79 | 99.03 | 99.05 | 99.01 | 98.81 | 98.58 | 98.2 | 98.51 | 98.6 | 98.54 | 98.33 | 98.01 | 97.56 | 98.01 | 98.15 | 98.17 | 97.96 | 97.63
Chint Power Systems America | CPS SCH125KTL-DO/US-600 | PV Inverter | 870 | 1000 | 1300 | 600 | 125 | CEC Inverter Database | 600V | Chint-Power-Systems-America-CPS-SCH125KTL-DO-US-600-600V | Y | 4.9 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.7077 | 99.0329 | 99.0691 | 98.9523 | 98.7899 | 98.5613 | 98.1008 | 98.563 | 98.5841 | 98.5384 | 98.352 | 98.0513 | 97.4171 | 98.0383 | 98.14 | 98.1411 | 97.9782 | 97.6992
Darfon Electronics Corp. | H5001xxxxxx | PV Inverter | 300 | 360 | 380 | 240 | 4.844 | CEC Inverter Database | 240V | Darfon-Electronics-Corp.-H5001xxxxxx-240V | Y | 28.48 | 0.48442 | 0.96883 | 1.4533 | 2.4221 | 3.6331 | 4.8442 | 86.6736 | 92.8161 | 94.3502 | 95.2023 | 95.0579 | 94.4449 | 87.1365 | 93.1676 | 94.6479 | 95.4859 | 95.3797 | 94.8013 | 87.1729 | 93.1946 | 94.6523 | 95.4841 | 95.3494 | 94.7714
Darfon Electronics Corp. | H5000xxxxxx | PV Inverter | 300 | 360 | 380 | 240 | 5.074 | CEC Inverter Database | 240V | Darfon-Electronics-Corp.-H5000xxxxxx-240V | Y | 0.43 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196
Delta Electronics | SOLIVIA 3.8 NA G4 TL | PV Inverter | 100 | 380 | 500 | 208 | 3.32 | CEC Inverter Database | 208V | Delta-Electronics-SOLIVIA-3.8-NA-G4-TL-208V | Y | 1.14 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1
Delta Electronics | M4-TL-US | PV Inverter | 180 | 380 | 480 | 208 | 3.33 | CEC Inverter Database | 208V | Delta-Electronics-M4-TL-US-208V | Y | 1.92 | 0.3328 | 0.6656 | 0.9984 | 1.664 | 2.496 | 3.328 | 92 | 94.6 | 95.7 | 96.5 | 96.7 | 96.5 | 93 | 95.7 | 97.3 | 97.3 | 97.8 | 97.4 | 92.9 | 95.9 | 96.8 | 97.5 | 97.6 | 97.5
Delta Electronics | E4-TL-US | PV Inverter | 200 | 380 | 480 | 208 | 3.36 | CEC Inverter Database | 208V | Delta-Electronics-E4-TL-US-208V | Y | 1.21 | 0.33599 | 0.67197 | 1.008 | 1.6799 | 2.5199 | 3.3599 | 92.7058 | 95.316 | 96.0794 | 96.9375 | 97.261 | 97.2579 | 94.6716 | 96.7433 | 97.431 | 97.8832 | 97.9342 | 97.8306 | 93.5334 | 96.0786 | 96.9192 | 97.5645 | 97.7603 | 97.6747
Delta Electronics | SOLIVIA 3.8 NA G4 TL | PV Inverter | 100 | 380 | 500 | 240 | 3.81 | CEC Inverter Database | 240V | Delta-Electronics-SOLIVIA-3.8-NA-G4-TL-240V | Y | 1.19 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6
Delta Electronics | M4-TL-US | PV Inverter | 180 | 380 | 480 | 240 | 3.84 | CEC Inverter Database | 240V | Delta-Electronics-M4-TL-US-240V | Y | 2.03 | 0.384 | 0.768 | 1.152 | 1.92 | 2.88 | 3.84 | 92.9 | 95.1 | 96.1 | 96.9 | 96.9 | 96.7 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 93.6 | 96.4 | 97.2 | 97.7 | 97.8 | 97.7
Delta Electronics | E4-TL-US | PV Inverter | 200 | 380 | 400 | 240 | 3.87 | CEC Inverter Database | 240V | Delta-Electronics-E4-TL-US-240V | Y | 1.27 | 0.38696 | 0.77392 | 1.1609 | 1.9348 | 2.9022 | 3.8696 | 92.8573 | 95.3032 | 96.0816 | 97.008 | 97.3433 | 97.3609 | 95.3025 | 97.1049 | 97.7261 | 98.0933 | 98.1429 | 98.1114 | 94.285 | 96.4536 | 97.2773 | 97.8608 | 98.0038 | 97.9448
Delta Electronics | M5-TL-US | PV Inverter | 220 | 380 | 480 | 208 | 4.16 | CEC Inverter Database | 208V | Delta-Electronics-M5-TL-US-208V | Y | 1.24 | 0.416 | 0.832 | 1.248 | 2.08 | 3.12 | 4.16 | 94.5 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 95.8 | 97.3 | 97.8 | 98 | 97.8 | 97.6 | 95 | 96.8 | 97.4 | 97.7 | 97.7 | 97.4
Delta Electronics | M5-TL-US | PV Inverter | 220 | 380 | 480 | 240 | 4.86 | CEC Inverter Database | 240V | Delta-Electronics-M5-TL-US-240V | Y | 1.26 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 94.3 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 96.3 | 97.6 | 98 | 98.2 | 98 | 97.8 | 95.6 | 97.2 | 97.7 | 98 | 97.9 | 97.7
Delta Electronics | M6-TL-US | PV Inverter | 200 | 380 | 480 | 208 | 4.99 | CEC Inverter Database | 208V | Delta-Electronics-M6-TL-US-208V | Y | 1.86 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94 | 95.6 | 96.5 | 97 | 97 | 96.7 | 95.7 | 97.2 | 97.7 | 97.8 | 97.7 | 97.3 | 94.6 | 96.5 | 97.2 | 97.5 | 97.5 | 97.2
Delta Electronics | E6-TL-US | PV Inverter | 200 | 380 | 480 | 208 | 4.992 | CEC Inverter Database | 208V | Delta-Electronics-E6-TL-US-208V | Y | 1.86 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94.0016 | 95.6485 | 96.4705 | 97.0318 | 96.9884 | 96.6789 | 95.696 | 97.2204 | 97.6522 | 97.8362 | 97.6671 | 97.3491 | 94.6317 | 96.517 | 97.1735 | 97.5416 | 97.4711 | 97.1739
Delta Electronics | SOLIVIA 5.2 NA G4 TL | PV Inverter | 100 | 380 | 500 | 208 | 5.2 | CEC Inverter Database | 208V | Delta-Electronics-SOLIVIA-5.2-NA-G4-TL-208V | Y | 1.31 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5
Delta Electronics | SOLIVIA 5.2 NA G4 TL | PV Inverter | 100 | 380 | 500 | 240 | 5.2 | CEC Inverter Database | 240V | Delta-Electronics-SOLIVIA-5.2-NA-G4-TL-240V | Y | 1.42 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98
Delta Electronics | E6-TL-US | PV Inverter | 200 | 380 | 480 | 240 | 5.76 | CEC Inverter Database | 240V | Delta-Electronics-E6-TL-US-240V | Y | 2.25 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.9636 | 95.7324 | 96.5328 | 97.1183 | 97.0624 | 96.7746 | 96.2574 | 97.615 | 97.9819 | 98.0814 | 97.6804 | 97.6267 | 95.2386 | 96.9825 | 97.5357 | 97.8342 | 97.7548 | 97.4585
Delta Electronics | M6-TL-US | PV Inverter | 200 | 380 | 480 | 240 | 5.76 | CEC Inverter Database | 240V | Delta-Electronics-M6-TL-US-240V | Y | 2.25 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 94 | 95.7 | 96.5 | 97.1 | 97.1 | 96.8 | 96.3 | 97.6 | 98 | 98.1 | 97.7 | 97.6 | 95.2 | 97 | 97.5 | 97.8 | 97.8 | 97.5
Delta Electronics | SOLIVIA 6.6 NA G4 TL | PV Inverter | 100 | 380 | 500 | 208 | 6.6 | CEC Inverter Database | 208V | Delta-Electronics-SOLIVIA-6.6-NA-G4-TL-208V | Y | 1.23 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1
Delta Electronics | SOLIVIA 6.6 NA G4 TL | PV Inverter | 100 | 380 | 500 | 240 | 6.6 | CEC Inverter Database | 240V | Delta-Electronics-SOLIVIA-6.6-NA-G4-TL-240V | Y | 1.45 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7
Delta Electronics | SOLIVIA 7.6 NA G4 TL | PV Inverter | 100 | 380 | 500 | 208 | 6.6 | CEC Inverter Database | 208V | Delta-Electronics-SOLIVIA-7.6-NA-G4-TL-208V | Y | 1.23 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1
Delta Electronics | E8-TL-US | PV Inverter | 270 | 380 | 480 | 208 | 6.656 | CEC Inverter Database | 208V | Delta-Electronics-E8-TL-US-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2308 | 96.891 | 97.3835 | 97.6343 | 97.4276 | 97.0506 | 95.9476 | 97.4104 | 97.7946 | 97.9487 | 97.6997 | 97.3918 | 94.855 | 96.7763 | 97.3739 | 97.6604 | 97.5174 | 97.1621
Delta Electronics | M8-TL-US | PV Inverter | 270 | 380 | 480 | 208 | 6.66 | CEC Inverter Database | 208V | Delta-Electronics-M8-TL-US-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 95.9 | 97.4 | 97.8 | 97.9 | 97.7 | 97.4 | 94.9 | 96.8 | 97.4 | 97.7 | 97.5 | 97.2
Delta Electronics | SOLIVIA 7.6 NA G4 TL | PV Inverter | 100 | 380 | 500 | 240 | 7.6 | CEC Inverter Database | 240V | Delta-Electronics-SOLIVIA-7.6-NA-G4-TL-240V | Y | 1.43 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5
Delta Electronics | E8-TL-US | PV Inverter | 270 | 380 | 480 | 240 | 7.68 | CEC Inverter Database | 240V | Delta-Electronics-E8-TL-US-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2202 | 96.7865 | 97.3605 | 97.6615 | 97.5147 | 97.0633 | 96.5571 | 97.7682 | 98.0917 | 98.1644 | 97.9971 | 97.6404 | 95.5533 | 97.2136 | 97.7339 | 97.9476 | 97.8481 | 97.5018
Delta Electronics | M8-TL-US | PV Inverter | 270 | 380 | 480 | 240 | 7.68 | CEC Inverter Database | 240V | Delta-Electronics-M8-TL-US-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2 | 96.8 | 97.4 | 97.7 | 97.5 | 97.1 | 96.6 | 97.8 | 98.1 | 98.2 | 98 | 97.6 | 95.6 | 97.2 | 97.7 | 97.9 | 97.8 | 97.5
Delta Electronics | M10-TL-US | PV Inverter | 280 | 380 | 480 | 208 | 8.36 | CEC Inverter Database | 208V | Delta-Electronics-M10-TL-US-208V | Y | 1.35 | 0.836 | 1.672 | 2.508 | 4.18 | 6.27 | 8.36 | 95.6582 | 97.2037 | 97.6275 | 97.6939 | 97.3331 | 96.7189 | 96.1037 | 97.4684 | 97.8423 | 97.88 | 97.4815 | 96.939 | 95.3231 | 96.9699 | 97.4951 | 97.6758 | 97.379 | 96.7989
Delta Electronics | M10-4-TL-US | PV Inverter | 280 | 350 | 480 | 208 | 8.385 | CEC Inverter Database | 208V | Delta-Electronics-M10-4-TL-US-208V | Y | 1.35 | 0.83848 | 1.677 | 2.5154 | 4.1924 | 6.2886 | 8.3848 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 96.735 | 97.5607 | 97.6985 | 97.6022 | 97.3608 | 97.0685 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273
Delta Electronics | M10-TL-US | PV Inverter | 280 | 380 | 480 | 240 | 9.62 | CEC Inverter Database | 240V | Delta-Electronics-M10-TL-US-240V | Y | 1.41 | 0.96203 | 1.9241 | 2.8861 | 4.8101 | 7.2152 | 9.6203 | 95.8434 | 97.2454 | 97.6952 | 97.7815 | 97.4547 | 96.8686 | 96.6236 | 97.7885 | 98.0915 | 98.1079 | 97.7286 | 97.0794 | 95.9166 | 97.3593 | 97.8019 | 97.9562 | 97.6575 | 97.2218
Delta Electronics | M10-4-TL-US | PV Inverter | 280 | 380 | 480 | 240 | 9.674 | CEC Inverter Database | 240V | Delta-Electronics-M10-4-TL-US-240V | Y | 1.38 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601
Delta Electronics | M24U_120 | PV Inverter | 415 | 710 | 830 | 480 | 26.403 | CEC Inverter Database | 480V | Delta-Electronics-M24U_120-480V | Y | 2.6 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27
Delta Electronics | M24U_121 | PV Inverter | 415 | 710 | 830 | 480 | 26.403 | CEC Inverter Database | 480V | Delta-Electronics-M24U_121-480V | Y | 2.6 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27
Delta Electronics | M24U_122 | PV Inverter | 415 | 710 | 830 | 480 | 26.403 | CEC Inverter Database | 480V | Delta-Electronics-M24U_122-480V | Y | 2.6 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27
Delta Electronics | E30-TL | PV Inverter | 515 | 750 | 830 | 277 | 30.488 | CEC Inverter Database | 277V | Delta-Electronics-E30-TL-277V | Y | 1.59 | 3.0488 | 6.0975 | 9.1463 | 15.2438 | 22.8657 | 30.4876 | 95.9222 | 97.1353 | 97.5449 | 97.7515 | 97.701 | 97.4796 | 97.4461 | 98.3209 | 98.5555 | 98.6266 | 98.581 | 98.4647 | 96.9725 | 98.1055 | 98.382 | 98.4809 | 98.4516 | 98.3166
Delta Electronics | M28U_120 | PV Inverter | 485 | 710 | 830 | 480 | 30.709 | CEC Inverter Database | 480V | Delta-Electronics-M28U_120-480V | Y | 2.4 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18
Delta Electronics | M28U_121 | PV Inverter | 485 | 710 | 830 | 480 | 30.709 | CEC Inverter Database | 480V | Delta-Electronics-M28U_121-480V | Y | 2.4 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18
Delta Electronics | M28U_122 | PV Inverter | 485 | 710 | 830 | 480 | 30.709 | CEC Inverter Database | 480V | Delta-Electronics-M28U_122-480V | Y | 2.4 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18
Delta Electronics | M36U_120 | PV Inverter | 520 | 710 | 830 | 480 | 39.737 | CEC Inverter Database | 480V | Delta-Electronics-M36U_120-480V | Y | 2.9 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95
Delta Electronics | M36U_121 | PV Inverter | 520 | 710 | 830 | 480 | 39.737 | CEC Inverter Database | 480V | Delta-Electronics-M36U_121-480V | Y | 2.9 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95
Delta Electronics | M36U_122 | PV Inverter | 520 | 710 | 830 | 480 | 39.737 | CEC Inverter Database | 480V | Delta-Electronics-M36U_122-480V | Y | 2.9 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95
Delta Electronics | M42U_120 | PV Inverter | 545 | 710 | 830 | 480 | 45.972 | CEC Inverter Database | 480V | Delta-Electronics-M42U_120-480V | Y | 2.9 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86
Delta Electronics | M42U_121 | PV Inverter | 545 | 710 | 830 | 480 | 45.972 | CEC Inverter Database | 480V | Delta-Electronics-M42U_121-480V | Y | 2.9 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86
Delta Electronics | M42U_122 | PV Inverter | 545 | 710 | 830 | 480 | 45.972 | CEC Inverter Database | 480V | Delta-Electronics-M42U_122-480V | Y | 2.9 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86
Delta Electronics | M60U_120 | PV Inverter | 540 | 710 | 800 | 480 | 65.47 | CEC Inverter Database | 480V | Delta-Electronics-M60U_120-480V | Y | 2.863 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14
Delta Electronics | M60U_121 | PV Inverter | 540 | 710 | 800 | 480 | 65.47 | CEC Inverter Database | 480V | Delta-Electronics-M60U_121-480V | Y | 2.863 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14
Delta Electronics | M60U_122 | PV Inverter | 540 | 710 | 800 | 480 | 65.47 | CEC Inverter Database | 480V | Delta-Electronics-M60U_122-480V | Y | 2.863 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14
Delta Electronics | M80U_120 | PV Inverter | 600 | 710 | 800 | 480 | 82.764 | CEC Inverter Database | 480V | Delta-Electronics-M80U_120-480V | Y | 2.6 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09
Delta Electronics | M80U_121 | PV Inverter | 600 | 710 | 800 | 480 | 82.764 | CEC Inverter Database | 480V | Delta-Electronics-M80U_121-480V | Y | 2.6 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09
Delta Electronics | M80U_122 | PV Inverter | 600 | 710 | 800 | 480 | 82.764 | CEC Inverter Database | 480V | Delta-Electronics-M80U_122-480V | Y | 2.6 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09
Delta Electronics | M125HV | PV Inverter | 860 | 1000 | 1200 | 600 | 124.468 | CEC Inverter Database | 600V | Delta-Electronics-M125HV-600V | Y | 0 | 12.4468 | 24.8937 | 37.3405 | 62.2342 | 93.3513 | 124.4684 | 98.918 | 99.156 | 99.1897 | 99.102 | 98.848 | 98.528 | 98.3448 | 98.786 | 98.866 | 98.9082 | 98.8042 | 98.344 | 97.694 | 98.374 | 98.5076 | 98.648 | 98.5836 | 98.2445
Destin Power Inc. | SAVEEN1000-ES02H.US | PV Inverter | 740 | 830 | 900 | 440 | 1000 | CEC Inverter Database | 440V | Destin-Power-Inc.-SAVEEN1000-ES02H.US-440V | Y | 149.25 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.9762 | 97.2102 | 97.9516 | 98.4084 | 98.507 | 98.421 | 94.252 | 96.7644 | 97.5816 | 98.1856 | 98.3254 | 98.2608 | 93.5872 | 96.4774 | 97.3838 | 98.0058 | 98.2088 | 98.1694
Enphase Energy Inc. | IQ7PD-72-2-US | PV Inverter | 22 | 31 | 40 | 208 | 0.191 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PD-72-2-US-208V | Y | 0.02 | 0.019078 | 0.038156 | 0.057235 | 0.095391 | 0.14309 | 0.19078 | 93.458 | 94.6122 | 96.5408 | 97.2243 | 97.1303 | 96.6782 | 94.1892 | 95.57 | 95.9456 | 97.2425 | 97.4304 | 97.3251 | 93.1764 | 94.4298 | 95.4021 | 96.9211 | 97.2222 | 97.2054
Enphase Energy Inc. | IQ7PD-72-2-US | PV Inverter | 22 | 31 | 40 | 240 | 0.191 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PD-72-2-US-240V | Y | 0.02 | 0.019148 | 0.038295 | 0.057443 | 0.095739 | 0.14361 | 0.19148 | 92.9696 | 93.86 | 96.119 | 97.0685 | 96.9972 | 96.5816 | 94.3225 | 95.6189 | 95.3973 | 97.2206 | 97.52 | 97.5293 | 93.1596 | 94.4484 | 94.7891 | 96.8124 | 97.2752 | 97.4069
Enphase Energy Inc. | IQ7PD-84-2-US | PV Inverter | 31 | 40 | 50 | 208 | 0.211 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PD-84-2-US-208V | Y | 0.021 | 0.021144 | 0.042288 | 0.063432 | 0.10572 | 0.15858 | 0.21144 | 93.8312 | 95.0289 | 96.0923 | 97.0931 | 97.1677 | 96.9428 | 93.1896 | 94.8072 | 95.5863 | 96.8088 | 96.9807 | 96.8462 | 92.3854 | 93.9263 | 95.0054 | 96.5139 | 96.7794 | 96.7231
Enphase Energy Inc. | IQ7PD-84-2-US | PV Inverter | 31 | 40 | 50 | 240 | 0.211 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PD-84-2-US-240V | Y | 0.022 | 0.021137 | 0.042273 | 0.06341 | 0.10568 | 0.15853 | 0.21137 | 94.0019 | 95.0964 | 96.2205 | 97.3342 | 97.5296 | 97.4271 | 93.5498 | 95.2306 | 95.6885 | 96.9745 | 97.3031 | 97.3583 | 92.5204 | 94.3275 | 94.8974 | 96.6419 | 97.0503 | 97.1852
Enphase Energy Inc. | S230-60-LL-x | PV Inverter | 27 | 32 | 37 | 208 | 0.22 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-S230-60-LL-x-208V | Y | 0.051 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 94.9 | 96.5 | 96.4 | 97.2 | 97.2 | 96.9 | 94.9 | 96.4 | 96.1 | 97.1 | 97.1 | 96.8 | 94.8 | 96.3 | 95.8 | 96.9 | 97 | 96.7
Enphase Energy Inc. | S230-60-LL-x | PV Inverter | 27 | 32 | 37 | 240 | 0.22 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-S230-60-LL-x-240V | Y | 0.051 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 95 | 96.4 | 96.2 | 97.4 | 97.5 | 97.4 | 95 | 96.5 | 95.8 | 97.2 | 97.3 | 97.2 | 94.9 | 96.4 | 95.4 | 96.9 | 97.2 | 97.2
Enphase Energy Inc. | IQ6-60-2-US | PV Inverter | 27 | 32 | 37 | 208 | 0.23 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6-60-2-US-208V | Y | 0.02 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175
Enphase Energy Inc. | IQ6-60-2-US | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6-60-2-US-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Enphase Energy Inc. | IQ6-60-5-US | PV Inverter | 27 | 32 | 37 | 208 | 0.23 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6-60-5-US-208V | Y | 0.02 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175
Enphase Energy Inc. | IQ6-60-5-US | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6-60-5-US-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Enphase Energy Inc. | IQ6-60-ACM-US | PV Inverter | 27 | 32 | 37 | 208 | 0.23 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6-60-ACM-US-208V | Y | 0.02 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175
Enphase Energy Inc. | IQ6-60-ACM-US | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6-60-ACM-US-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Enphase Energy Inc. | IQ7-60-2-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-2-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-2-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-2-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-5-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-5-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-5-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-5-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-ACM-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-ACM-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-ACM-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-ACM-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-ACM-US-NM | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-ACM-US-NM-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-ACM-US-NM | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-ACM-US-NM-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-E-ACM-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-E-ACM-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-E-ACM-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-E-ACM-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-E-ACM-US-NM | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-E-ACM-US-NM-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-E-ACM-US-NM | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-E-ACM-US-NM-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-E-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-E-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-E-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-E-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ7-60-M-US | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7-60-M-US-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | IQ7-60-M-US | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7-60-M-US-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6587 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-300M | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-XACM-IQ7-LR6-60PB-300M-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-300M | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-XACM-IQ7-LR6-60PB-300M-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-305M | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-XACM-IQ7-LR6-60PB-305M-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-305M | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-XACM-IQ7-LR6-60PB-305M-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Enphase Energy Inc. | IQ8-60-2-US | PV Inverter | 27 | 32 | 40 | 240 | 0.242 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8-60-2-US-240V | Y | 0.033 | 0.024243 | 0.048486 | 0.072729 | 0.12122 | 0.18182 | 0.24243 | 93.4667 | 93.5875 | 95.83 | 96.8229 | 96.5746 | 95.9549 | 95.0586 | 96.4215 | 96.7604 | 97.1679 | 97.1747 | 96.8617 | 95.5625 | 96.5258 | 96.8739 | 97.2638 | 97.4936 | 97.414
Enphase Energy Inc. | IQ8-60-M-US | PV Inverter | 27 | 32 | 40 | 240 | 0.242 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8-60-M-US-240V | Y | 0.033 | 0.024243 | 0.048486 | 0.072729 | 0.12122 | 0.18182 | 0.24243 | 93.4667 | 93.5875 | 95.83 | 96.8229 | 96.5746 | 95.9549 | 95.0586 | 96.4215 | 96.7604 | 97.1679 | 97.1747 | 96.8617 | 95.5625 | 96.5258 | 96.8739 | 97.2638 | 97.4936 | 97.414
Enphase Energy Inc. | IQ6PLUS-ACB-LL | PV Inverter | 23 | 25 | 28 | 240 | 0.27 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6PLUS-ACB-LL-240V | Y | 0.07 | 0.027 | 0.054 | 0.081 | 0.135 | 0.2025 | 0.27 | 85.8903 | 93.6164 | 95.4627 | 95.9769 | 95.5783 | 94.8032 | 85.8003 | 93.4691 | 95.4058 | 96.1485 | 95.8765 | 95.2295 | 85.5189 | 93.1183 | 95.1904 | 96.1928 | 96.0669 | 95.5951
Enphase Energy Inc. | S280-60-LL-x | PV Inverter | 27 | 32 | 37 | 208 | 0.27 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-S280-60-LL-x-208V | Y | 0.051 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95 | 96.1 | 96.5 | 96.9 | 96.7 | 96.2 | 95 | 96.1 | 96.1 | 96.7 | 96.6 | 96.2 | 94.9 | 95.7 | 95.8 | 96.6 | 96.5 | 96.1
Enphase Energy Inc. | S280-60-LL-x | PV Inverter | 27 | 32 | 37 | 240 | 0.27 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-S280-60-LL-x-240V | Y | 0.062 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95.2 | 96.5 | 96.9 | 97.3 | 97.3 | 97 | 95.3 | 96.5 | 96.7 | 97.1 | 97.2 | 96.9 | 95.1 | 96.1 | 96 | 96.9 | 97.1 | 96.9
Enphase Energy Inc. | IQ6PLUS-72-2-US | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6PLUS-72-2-US-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595
Enphase Energy Inc. | IQ6PLUS-72-2-US | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6PLUS-72-2-US-240V | Y | 0.03 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384
Enphase Energy Inc. | IQ6PLUS-72-5-US | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6PLUS-72-5-US-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595
Enphase Energy Inc. | IQ6PLUS-72-5-US | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6PLUS-72-5-US-240V | Y | 0.03 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384
Enphase Energy Inc. | IQ6PLUS-72-ACM-US | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ6PLUS-72-ACM-US-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595
Enphase Energy Inc. | IQ6PLUS-72-ACM-US | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ6PLUS-72-ACM-US-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384
Enphase Energy Inc. | IQ7PLUS-72-2-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-2-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-2-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-2-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-5-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-5-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-5-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-5-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-ACM-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-ACM-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-ACM-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-ACM-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-ACM-US-NM | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-ACM-US-NM-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-ACM-US-NM | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-ACM-US-NM-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-E-ACM-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-E-ACM-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-E-ACM-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-E-ACM-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-E-ACM-US-NM | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-E-ACM-US-NM-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-E-ACM-US-NM | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-E-ACM-US-NM-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-E-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-E-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-E-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-E-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7PLUS-72-M-US | PV Inverter | 27 | 36 | 45 | 208 | 0.29 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7PLUS-72-M-US-208V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734
Enphase Energy Inc. | IQ7PLUS-72-M-US | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7PLUS-72-M-US-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Enphase Energy Inc. | IQ7A-66-x-US-& | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-66-x-US-&-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-2-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-2-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-5-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-5-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-E-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-E-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-M-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-M-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-2-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-2-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-5-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-5-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-E-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-E-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-66-x-ACM-US-y-z-& | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-66-x-ACM-US-y-z-&-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-ACM-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-E-ACM-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7A-72-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7A-72-E-ACM-US-NM-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-NM-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-ACM-US-RMA | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-RMA-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-E-ACM-US-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7AS-66-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 208 | 0.29291 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7AS-66-E-ACM-US-NM-208V | Y | 0.045 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939
Enphase Energy Inc. | IQ7GPLUS-72-2-US | PV Inverter | 29 | 37 | 45 | 240 | 0.298 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7GPLUS-72-2-US-240V | Y | 0.03 | 0.029767 | 0.059535 | 0.089302 | 0.14884 | 0.22326 | 0.29767 | 94.9075 | 94.778 | 96.6298 | 97.1774 | 96.7309 | 96.309 | 95.4932 | 96.8423 | 96.4128 | 97.5518 | 97.4968 | 97.2122 | 95.8204 | 96.8733 | 96.9766 | 97.5159 | 97.6552 | 97.4534
Enphase Energy Inc. | IQ8PLUS-72-2-US | PV Inverter | 29 | 37 | 45 | 240 | 0.298 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8PLUS-72-2-US-240V | Y | 0.03 | 0.029767 | 0.059535 | 0.089302 | 0.14884 | 0.22326 | 0.29767 | 94.9075 | 94.778 | 96.6298 | 97.1774 | 96.7309 | 96.309 | 95.4932 | 96.8423 | 96.4128 | 97.5518 | 97.4968 | 97.2122 | 95.8204 | 96.8733 | 96.9766 | 97.5159 | 97.6552 | 97.4534
Enphase Energy Inc. | IQ8PLUS-72-M-US | PV Inverter | 29 | 37 | 45 | 240 | 0.298 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8PLUS-72-M-US-240V | Y | 0.03 | 0.029767 | 0.059535 | 0.089302 | 0.14884 | 0.22326 | 0.29767 | 94.9075 | 94.778 | 96.6298 | 97.1774 | 96.7309 | 96.309 | 95.4932 | 96.8423 | 96.4128 | 97.5518 | 97.4968 | 97.2122 | 95.8204 | 96.8733 | 96.9766 | 97.5159 | 97.6552 | 97.4534
Enphase Energy Inc. | IQ7X-96-2-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-2-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-2-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-2-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-5-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-5-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-5-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-5-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-ACM-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-ACM-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-ACM-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-ACM-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-ACM-US-NM-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-ACM-US-NM-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-E-ACM-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-E-ACM-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-E-ACM-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-E-ACM-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-E-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-E-ACM-US-NM-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-E-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-E-ACM-US-NM-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-E-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-E-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-E-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-E-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7X-96-M-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7X-96-M-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7X-96-M-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7X-96-M-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-2-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-2-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-2-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-2-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-5-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-5-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-5-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-5-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-ACM-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-ACM-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-NM-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-NM-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-ACM-US-RMA | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-RMA-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-ACM-US-RMA | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-ACM-US-RMA-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-E-ACM-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-E-ACM-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-E-ACM-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-E-ACM-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-E-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-E-ACM-US-NM-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-E-ACM-US-NM | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-E-ACM-US-NM-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ7XS-96-E-US | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7XS-96-E-US-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
Enphase Energy Inc. | IQ7XS-96-E-US | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7XS-96-E-US-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Enphase Energy Inc. | IQ8M-72-2-US | PV Inverter | 33 | 39 | 45 | 240 | 0.327 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8M-72-2-US-240V | Y | 0.028 | 0.03268 | 0.06536 | 0.09804 | 0.1634 | 0.2451 | 0.3268 | 95.8696 | 96.7898 | 96.8061 | 97.5021 | 97.2285 | 96.7309 | 96.1374 | 96.7886 | 96.7328 | 97.5848 | 97.4467 | 97.1298 | 96.1263 | 96.9463 | 96.3583 | 97.5601 | 97.5624 | 97.3113
Enphase Energy Inc. | IQ8M-72-M-US | PV Inverter | 33 | 39 | 45 | 240 | 0.327 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8M-72-M-US-240V | Y | 0.028 | 0.03268 | 0.06536 | 0.09804 | 0.1634 | 0.2451 | 0.3268 | 95.8696 | 96.7898 | 96.8061 | 97.5021 | 97.2285 | 96.7309 | 96.1374 | 96.7886 | 96.7328 | 97.5848 | 97.4467 | 97.1298 | 96.1263 | 96.9463 | 96.3583 | 97.5601 | 97.5624 | 97.3113
Enphase Energy Inc. | IQ7A-66-x-US-& | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-66-x-US-&-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-2-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-2-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-5-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-5-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-E-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-E-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-M-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-M-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-2-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-2-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-5-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-5-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-E-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-E-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-66-x-ACM-US-y-z-& | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-66-x-ACM-US-y-z-&-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-ACM-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-E-ACM-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7A-72-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7A-72-E-ACM-US-NM-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-NM-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-ACM-US-RMA | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-ACM-US-RMA-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-E-ACM-US-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ7AS-66-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7AS-66-E-ACM-US-NM-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Enphase Energy Inc. | IQ8A-72-2-US | PV Inverter | 36 | 40.5 | 45 | 240 | 0.354 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8A-72-2-US-240V | Y | 0.028 | 0.035386 | 0.070771 | 0.10616 | 0.17693 | 0.26539 | 0.35386 | 96.0633 | 96.9258 | 97.0675 | 97.5678 | 97.2381 | 96.6854 | 96.0254 | 97.0177 | 96.9593 | 97.6666 | 97.4998 | 97.055 | 96.0977 | 96.9939 | 97.2598 | 97.6506 | 97.5758 | 97.2289
Enphase Energy Inc. | IQ8A-72-M-US | PV Inverter | 36 | 40.5 | 45 | 240 | 0.354 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8A-72-M-US-240V | Y | 0.028 | 0.035386 | 0.070771 | 0.10616 | 0.17693 | 0.26539 | 0.35386 | 96.0633 | 96.9258 | 97.0675 | 97.5678 | 97.2381 | 96.6854 | 96.0254 | 97.0177 | 96.9593 | 97.6666 | 97.4998 | 97.055 | 96.0977 | 96.9939 | 97.2598 | 97.6506 | 97.5758 | 97.2289
Enphase Energy Inc. | IQ8H-208-72-2-US | PV Inverter | 38 | 41.5 | 45 | 208 | 0.361 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ8H-208-72-2-US-208V | Y | 0.02 | 0.036056 | 0.072111 | 0.10817 | 0.18028 | 0.27042 | 0.36056 | 96.1665 | 96.9404 | 97.1948 | 97.4385 | 96.9787 | 96.3858 | 96.1987 | 96.8772 | 97.0833 | 97.4283 | 97.0547 | 96.4899 | 96.0938 | 96.7106 | 96.9641 | 97.3793 | 97.0418 | 96.5108
Enphase Energy Inc. | IQ8H-208-72-M-US | PV Inverter | 38 | 41.5 | 45 | 208 | 0.361 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ8H-208-72-M-US-208V | Y | 0.02 | 0.036056 | 0.072111 | 0.10817 | 0.18028 | 0.27042 | 0.36056 | 96.1665 | 96.9404 | 97.1948 | 97.4385 | 96.9787 | 96.3858 | 96.1987 | 96.8772 | 97.0833 | 97.4283 | 97.0547 | 96.4899 | 96.0938 | 96.7106 | 96.9641 | 97.3793 | 97.0418 | 96.5108
Enphase Energy Inc. | IQ7HS-66-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7HS-66-ACM-US-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
Enphase Energy Inc. | IQ7HS-66-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7HS-66-ACM-US-NM-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
Enphase Energy Inc. | IQ7HS-66-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7HS-66-E-ACM-US-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
Enphase Energy Inc. | IQ7HS-66-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | Enphase-Energy-Inc.-IQ7HS-66-E-ACM-US-NM-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
Enphase Energy Inc. | IQ8H-240-72-2-US | PV Inverter | 38 | 41.5 | 45 | 240 | 0.379 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8H-240-72-2-US-240V | Y | 0.028 | 0.037911 | 0.075822 | 0.11373 | 0.18956 | 0.28433 | 0.37911 | 96.2445 | 96.9978 | 97.1799 | 97.5091 | 97.059 | 96.5752 | 96.2117 | 96.9955 | 97.1307 | 97.5999 | 97.2795 | 96.9118 | 96.2922 | 96.9089 | 97.0011 | 97.5694 | 97.352 | 96.9748
Enphase Energy Inc. | IQ8H-240-72-M-US | PV Inverter | 38 | 41.5 | 45 | 240 | 0.379 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8H-240-72-M-US-240V | Y | 0.028 | 0.037911 | 0.075822 | 0.11373 | 0.18956 | 0.28433 | 0.37911 | 96.2445 | 96.9978 | 97.1799 | 97.5091 | 97.059 | 96.5752 | 96.2117 | 96.9955 | 97.1307 | 97.5999 | 97.2795 | 96.9118 | 96.2922 | 96.9089 | 97.0011 | 97.5694 | 97.352 | 96.9748
Enphase Energy Inc. | IQ7HS-66-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7HS-66-ACM-US-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
Enphase Energy Inc. | IQ7HS-66-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7HS-66-ACM-US-NM-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
Enphase Energy Inc. | IQ7HS-66-E-ACM-US | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7HS-66-E-ACM-US-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
Enphase Energy Inc. | IQ7HS-66-E-ACM-US-NM | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ7HS-66-E-ACM-US-NM-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
EPC Power Corp. | HY LC12/6-7 | PV Inverter | 455 | 475 | 600 | 480 | 220.033 | CEC Inverter Database | 480V | EPC-Power-Corp.-HY-LC12-6-7-480V | Y | 19.2 | 22.0033 | 44.0067 | 66.01 | 110.0167 | 165.025 | 220.0333 | 95.0157 | 96.16 | 96.4114 | 96.3571 | 96.0943 | 95.7657 | 93.9614 | 95.3957 | 95.6729 | 95.7343 | 95.5243 | 95.18 | 94.3386 | 95.8 | 96.0971 | 96.1657 | 96.0143 | 95.7186
Fronius International GmbH | Fronius Primo 3.8-1 208-240 | PV Inverter | 100 | 650 | 800 | 208 | 3.8 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-3.8-1-208-240-208V | Y | 0.41 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 87.3 | 92.4 | 93.9 | 95.2 | 95.6 | 95.7 | 90.7 | 95.2 | 96.4 | 97.2 | 97.5 | 97.6 | 85.7 | 93.4 | 95.2 | 96.6 | 97.1 | 97.3
Fronius International GmbH | Fronius Primo 3.8-1 208-240 | PV Inverter | 100 | 650 | 800 | 240 | 3.8 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-3.8-1-208-240-240V | Y | 0.55 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 85.5 | 91.5 | 93.3 | 94.8 | 95.4 | 95.6 | 87.2 | 93.4 | 95 | 96.4 | 96.9 | 97.2 | 87 | 93.7 | 95.5 | 96.9 | 97.4 | 97.6
Fronius International GmbH | Fronius Primo 5.0-1 208-240 | PV Inverter | 100 | 650 | 800 | 208 | 5 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-5.0-1-208-240-208V | Y | 0.41 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.4 | 93.8 | 94.8 | 95.8 | 96 | 96 | 92.5 | 96 | 96.8 | 97.5 | 97.6 | 97.6 | 89.3 | 94.6 | 96 | 97 | 97.3 | 97.4
Fronius International GmbH | Fronius Primo 5.0-1 208-240 | PV Inverter | 100 | 660 | 800 | 240 | 5 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-5.0-1-208-240-240V | Y | 0.55 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89 | 93.2 | 94.6 | 95.6 | 95.9 | 96 | 91.6 | 95.4 | 96.4 | 97.1 | 97.4 | 97.4 | 92.3 | 96 | 97 | 97.7 | 97.9 | 97.9
Fronius International GmbH | Fronius Primo 6.0-1 208-240 | PV Inverter | 100 | 660 | 800 | 208 | 6 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-6.0-1-208-240-208V | Y | 0.41 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 90.7 | 94.4 | 95.2 | 95.9 | 96 | 95.9 | 93.5 | 96.5 | 97.1 | 97.6 | 97.6 | 97.6 | 91 | 95.4 | 96.4 | 97.2 | 97.3 | 97.4
Fronius International GmbH | Fronius Primo 6.0-1 208-240 | PV Inverter | 100 | 660 | 800 | 240 | 6 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-6.0-1-208-240-240V | Y | 0.55 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 89.8 | 93.6 | 94.9 | 95.8 | 96 | 96 | 91.4 | 95.3 | 96.3 | 97 | 97.3 | 97.3 | 91.7 | 95.7 | 96.7 | 97.5 | 97.7 | 97.7
Fronius International GmbH | Fronius Primo 7.6-1 208-240 | PV Inverter | 100 | 660 | 800 | 208 | 7.6 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-7.6-1-208-240-208V | Y | 0.41 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.7 | 95.1 | 95.8 | 96.1 | 96.1 | 95.8 | 96 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | 94.1 | 96.7 | 97.3 | 97.6 | 97.5 | 97.4
Fronius International GmbH | Fronius Primo 7.6-1 208-240 | PV Inverter | 100 | 660 | 800 | 240 | 7.6 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-7.6-1-208-240-240V | Y | 0.55 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.6 | 94.8 | 95.5 | 96 | 96.1 | 95.9 | 94 | 96.4 | 97 | 97.4 | 97.5 | 97.4 | 94.6 | 97 | 97.6 | 97.9 | 97.9 | 97.8
Fronius International GmbH | Fronius Primo 8.2-1 208-240 | PV Inverter | 100 | 660 | 800 | 208 | 7.9 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-8.2-1-208-240-208V | Y | 0.41 | 0.79 | 1.58 | 2.37 | 3.95 | 5.93 | 7.9 | 93 | 95.3 | 95.9 | 96.2 | 96.2 | 95.9 | 95.8 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 94 | 96.7 | 97.3 | 97.6 | 97.6 | 97.4
Fronius International GmbH | Fronius Primo 8.2-1 208-240 | PV Inverter | 100 | 660 | 800 | 240 | 8.2 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-8.2-1-208-240-240V | Y | 0.55 | 0.82 | 1.64 | 2.46 | 4.1 | 6.15 | 8.2 | 92.1 | 94.9 | 95.7 | 96.2 | 96.2 | 96.1 | 94.2 | 96.6 | 97.1 | 97.4 | 97.4 | 97.4 | 94.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.8
Fronius International GmbH | Fronius Primo 10.0-1 208-240 | PV Inverter | 100 | 660 | 800 | 208 | 9.995 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-10.0-1-208-240-208V | Y | 0.24 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92 | 94.7 | 95.1 | 95.6 | 95.6 | 95.5 | 94.5 | 97.4 | 96.8 | 97.3 | 97.3 | 97.4 | 93.3 | 97.1 | 96.5 | 97 | 97.3 | 97.3
Fronius International GmbH | Fronius Primo 10.0-1 208-240 | PV Inverter | 100 | 655 | 800 | 240 | 9.995 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-10.0-1-208-240-240V | Y | 0.32 | 1 | 2 | 3 | 5 | 7.5 | 10 | 91.4 | 94.3 | 94.8 | 95.4 | 95.6 | 95.6 | 93.5 | 95.8 | 96.3 | 96.9 | 97.1 | 97 | 95.6 | 97 | 97.2 | 97.6 | 97.7 | 97.5
Fronius International GmbH | Fronius Symo 10.0-3 208-240 | PV Inverter | 100 | 370 | 480 | 208 | 9.995 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-10.0-3-208-240-208V | Y | 0.81 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7
Fronius International GmbH | Fronius Symo 10.0-3 208-240 | PV Inverter | 100 | 370 | 480 | 240 | 9.995 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-10.0-3-208-240-240V | Y | 0.8 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7
Fronius International GmbH | Fronius Symo 10.0-3 480 | PV Inverter | 100 | 670 | 800 | 480 | 9.995 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-10.0-3-480-480V | Y | 0.86 | 1 | 2 | 3 | 5 | 7.5 | 10 | 89.6 | 93.7 | 94.8 | 95.3 | 96 | 96.2 | 91.8 | 95.2 | 96.1 | 96.7 | 97.2 | 97.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.7 | 97.8
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 | PV Inverter | 300 | 355 | 480 | 208 | 10.011 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-Advanced-10.0-3-208-240-208V | Y | 0.6 | 1.0011 | 2.0021 | 3.0032 | 5.0053 | 7.508 | 10.0106 | 94.519 | 95.8999 | 96.162 | 96.1988 | 96.0327 | 95.7143 | 95.4147 | 96.5747 | 96.7816 | 96.8004 | 96.661 | 96.3996 | 94.3618 | 95.9714 | 96.3244 | 96.445 | 96.0917 | 96.1777
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 Lite | PV Inverter | 300 | 355 | 480 | 208 | 10.011 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-Advanced-10.0-3-208-240-Lite-208V | Y | 0.6 | 1.0011 | 2.0021 | 3.0032 | 5.0053 | 7.508 | 10.0106 | 94.519 | 95.8999 | 96.162 | 96.1988 | 96.0327 | 95.7143 | 95.4147 | 96.5747 | 96.7816 | 96.8004 | 96.661 | 96.3996 | 94.3618 | 95.9714 | 96.3244 | 96.445 | 96.0917 | 96.1777
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 | PV Inverter | 300 | 370 | 480 | 240 | 10.062 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-Advanced-10.0-3-208-240-240V | Y | 0.8 | 1.0062 | 2.0123 | 3.0185 | 5.0308 | 7.5462 | 10.0616 | 94.0092 | 95.6298 | 96.0803 | 96.2486 | 96.2138 | 96.0334 | 95.4049 | 96.7635 | 97.0499 | 97.1293 | 97.0789 | 96.9476 | 94.7759 | 96.3625 | 96.7198 | 96.8607 | 96.8774 | 96.7291
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 Lite | PV Inverter | 300 | 370 | 480 | 240 | 10.062 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-Advanced-10.0-3-208-240-Lite-240V | Y | 0.8 | 1.0062 | 2.0123 | 3.0185 | 5.0308 | 7.5462 | 10.0616 | 94.0092 | 95.6298 | 96.0803 | 96.2486 | 96.2138 | 96.0334 | 95.4049 | 96.7635 | 97.0499 | 97.1293 | 97.0789 | 96.9476 | 94.7759 | 96.3625 | 96.7198 | 96.8607 | 96.8774 | 96.7291
Fronius International GmbH | Fronius Primo 11.4-1 208-240 | PV Inverter | 240 | 660 | 800 | 208 | 11.4 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-11.4-1-208-240-208V | Y | 0.24 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 93 | 94.9 | 95.4 | 95.8 | 95.8 | 95.7 | 95.4 | 97 | 97.3 | 97.4 | 97.4 | 97.4 | 94.5 | 96.4 | 96.9 | 97.2 | 97.2 | 97.3
Fronius International GmbH | Fronius Primo 11.4-1 208-240 | PV Inverter | 240 | 660 | 800 | 240 | 11.4 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-11.4-1-208-240-240V | Y | 0.32 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 92.1 | 94.8 | 95.3 | 95.8 | 95.9 | 95.8 | 93.7 | 96.1 | 96.6 | 97 | 97.1 | 97.1 | 94.8 | 96.9 | 97.4 | 97.6 | 97.6 | 97.6
Fronius International GmbH | Fronius Symo 12.0-3 208-240 | PV Inverter | 300 | 350 | 480 | 208 | 12 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-12.0-3-208-240-208V | Y | 0.61 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 95.4 | 96.2 | 96.3 | 96.2 | 95.9 | 95.4 | 96.3 | 96.9 | 96.9 | 96.8 | 96.5 | 96.2 | 94.7 | 96.1 | 96.4 | 96.4 | 96.3 | 96
Fronius International GmbH | Fronius Symo 12.0-3 208-240 | PV Inverter | 300 | 370 | 480 | 240 | 12 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-12.0-3-208-240-240V | Y | 0.81 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 95.9 | 96.2 | 96.3 | 96.1 | 95.8 | 96 | 96.9 | 97.1 | 97.1 | 97 | 96.8 | 95.2 | 96.6 | 96.8 | 96.9 | 96.8 | 96.6
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 | PV Inverter | 300 | 370 | 480 | 240 | 12.09 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-Advanced-12.0-3-208-240-240V | Y | 0.8 | 1.209 | 2.418 | 3.6271 | 6.0451 | 9.0677 | 12.0902 | 94.3681 | 95.8926 | 96.1836 | 96.2592 | 96.1128 | 95.8185 | 95.9688 | 96.9444 | 97.0969 | 97.1128 | 97.001 | 96.8186 | 95.2352 | 96.577 | 96.7993 | 96.8786 | 96.7889 | 96.5969
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 Lite | PV Inverter | 300 | 370 | 480 | 240 | 12.09 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Symo-Advanced-12.0-3-208-240-Lite-240V | Y | 0.8 | 1.209 | 2.418 | 3.6271 | 6.0451 | 9.0677 | 12.0902 | 94.3681 | 95.8926 | 96.1836 | 96.2592 | 96.1128 | 95.8185 | 95.9688 | 96.9444 | 97.0969 | 97.1128 | 97.001 | 96.8186 | 95.2352 | 96.577 | 96.7993 | 96.8786 | 96.7889 | 96.5969
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 | PV Inverter | 300 | 350 | 480 | 208 | 12.341 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-Advanced-12.0-3-208-240-208V | Y | 0.61 | 1.2341 | 2.4682 | 3.7022 | 6.1704 | 9.2556 | 12.3408 | 95.3587 | 96.1848 | 96.2739 | 96.1814 | 95.8555 | 95.4107 | 96.2658 | 96.8639 | 96.9037 | 96.8162 | 96.5262 | 96.1647 | 94.7302 | 96.1208 | 96.3848 | 96.4459 | 96.2846 | 96.0009
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 Lite | PV Inverter | 300 | 350 | 480 | 208 | 12.341 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-Advanced-12.0-3-208-240-Lite-208V | Y | 0.61 | 1.2341 | 2.4682 | 3.7022 | 6.1704 | 9.2556 | 12.3408 | 95.3587 | 96.1848 | 96.2739 | 96.1814 | 95.8555 | 95.4107 | 96.2658 | 96.8639 | 96.9037 | 96.8162 | 96.5262 | 96.1647 | 94.7302 | 96.1208 | 96.3848 | 96.4459 | 96.2846 | 96.0009
Fronius International GmbH | Fronius Primo 12.5-1 208-240 | PV Inverter | 260 | 665 | 800 | 208 | 12.5 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-12.5-1-208-240-208V | Y | 0.24 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.5 | 95.1 | 95.5 | 95.9 | 95.9 | 95.6 | 95.3 | 96.9 | 97.3 | 97.5 | 97.3 | 97.3 | 94.5 | 96.6 | 97 | 97.2 | 97.1 | 97.2
Fronius International GmbH | Fronius Primo 12.5-1 208-240 | PV Inverter | 260 | 660 | 800 | 240 | 12.5 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-12.5-1-208-240-240V | Y | 0.32 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.1 | 95 | 95.4 | 95.9 | 95.9 | 95.8 | 93.7 | 96.2 | 96.6 | 97 | 97.1 | 97.1 | 95.4 | 97.2 | 97.3 | 97.5 | 97.6 | 97.7
Fronius International GmbH | Fronius Symo 12.5-3 480 | PV Inverter | 350 | 685 | 800 | 480 | 12.5 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-12.5-3-480-480V | Y | 0.94 | 1.25 | 2.5 | 3.75 | 6.25 | 9.37 | 12.5 | 92.5 | 94.9 | 95.6 | 96 | 96.4 | 96.5 | 94.4 | 96.5 | 97 | 97.3 | 97.5 | 97.5 | 95.6 | 97.3 | 97.7 | 97.9 | 98 | 98
Fronius International GmbH | Fronius Primo 15.0-1 208-240 | PV Inverter | 320 | 680 | 800 | 208 | 13.75 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Primo-15.0-1-208-240-208V | Y | 0.24 | 1.38 | 2.75 | 4.13 | 6.88 | 10.31 | 13.75 | 93.3 | 95.7 | 96 | 96.3 | 96.2 | 96 | 95.9 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 95.1 | 96.8 | 97.1 | 97.2 | 97.2 | 97.1
Fronius International GmbH | Fronius Primo 15.0-1 208-240 | PV Inverter | 320 | 680 | 800 | 240 | 15 | CEC Inverter Database | 240V | Fronius-International-GmbH-Fronius-Primo-15.0-1-208-240-240V | Y | 0.32 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.5 | 95.5 | 96 | 96.3 | 96.3 | 96.1 | 94.5 | 96.5 | 96.9 | 97.2 | 97.2 | 97 | 95.7 | 97.2 | 97.5 | 97.6 | 97.6 | 97.4
Fronius International GmbH | Fronius Symo 15.0-3 208 | PV Inverter | 325 | 445 | 800 | 208 | 15 | CEC Inverter Database | 208V | Fronius-International-GmbH-Fronius-Symo-15.0-3-208-208V | Y | 0.43 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 96.1 | 97 | 97.1 | 97.1 | 96.9 | 96.7 | 95.3 | 96.4 | 96.6 | 96.7 | 96.5 | 96.2 | 92.7 | 94.9 | 95.4 | 95.6 | 95.5 | 95.3
Fronius International GmbH | Fronius Symo 15.0-3 480 | PV Inverter | 350 | 685 | 800 | 480 | 15 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-15.0-3-480-480V | Y | 1.03 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 92 | 94.9 | 95.6 | 96.2 | 96.5 | 96.4 | 93.5 | 96 | 96.7 | 97.2 | 97.4 | 97.4 | 94.6 | 96.8 | 97.4 | 97.8 | 97.9 | 97.9
Fronius International GmbH | Fronius Symo Advanced 15.0-3 480 | PV Inverter | 350 | 685 | 800 | 480 | 15.197 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-15.0-3-480-480V | Y | 1 | 1.5197 | 3.0394 | 4.559 | 7.5984 | 11.3976 | 15.1968 | 92.0416 | 94.9196 | 95.6245 | 96.2374 | 96.4854 | 96.3871 | 93.544 | 95.9984 | 96.6963 | 97.2403 | 97.4077 | 97.4379 | 94.623 | 96.8127 | 97.3656 | 97.7693 | 97.8886 | 97.8973
Fronius International GmbH | Fronius Symo Advanced 15.0-3 480 Lite | PV Inverter | 350 | 685 | 800 | 480 | 15.197 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-15.0-3-480-Lite-480V | Y | 1 | 1.5197 | 3.0394 | 4.559 | 7.5984 | 11.3976 | 15.1968 | 92.0416 | 94.9196 | 95.6245 | 96.2374 | 96.4854 | 96.3871 | 93.544 | 95.9984 | 96.6963 | 97.2403 | 97.4077 | 97.4379 | 94.623 | 96.8127 | 97.3656 | 97.7693 | 97.8886 | 97.8973
Fronius International GmbH | Fronius Symo 17.5-3 480 | PV Inverter | 400 | 700 | 800 | 480 | 17.5 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-17.5-3-480-480V | Y | 1.03 | 1.75 | 3.5 | 5.25 | 8.75 | 13.12 | 17.5 | 92.7 | 95.3 | 95.8 | 96.5 | 96.6 | 96.7 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98.2 | 94.8 | 96.9 | 97.4 | 97.7 | 97.8 | 97.8
Fronius International GmbH | Fronius Symo 20.0-3 480 | PV Inverter | 450 | 712 | 800 | 480 | 20 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-20.0-3-480-480V | Y | 1.04 | 2 | 4 | 6 | 10 | 15 | 20 | 93.7 | 95.6 | 96.3 | 96.7 | 96.8 | 96.8 | 96 | 97.2 | 97.7 | 98 | 98 | 98 | 95.7 | 97 | 97.5 | 97.7 | 97.8 | 97.8
Fronius International GmbH | Fronius Symo Advanced 20.0-3 480 | PV Inverter | 450 | 710 | 800 | 480 | 20.227 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-20.0-3-480-480V | Y | 1 | 2.0227 | 4.0454 | 6.0681 | 10.1136 | 15.1704 | 20.2271 | 93.0613 | 95.4939 | 96.1422 | 96.7009 | 96.7849 | 96.8065 | 95.0962 | 97.0421 | 97.5307 | 97.8635 | 97.9715 | 98.0044 | 94.4625 | 96.6871 | 97.2645 | 97.6594 | 97.7318 | 97.7681
Fronius International GmbH | Fronius Symo Advanced 20.0-3 480 Lite | PV Inverter | 450 | 710 | 800 | 480 | 20.227 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-20.0-3-480-Lite-480V | Y | 1 | 2.0227 | 4.0454 | 6.0681 | 10.1136 | 15.1704 | 20.2271 | 93.0613 | 95.4939 | 96.1422 | 96.7009 | 96.7849 | 96.8065 | 95.0962 | 97.0421 | 97.5307 | 97.8635 | 97.9715 | 98.0044 | 94.4625 | 96.6871 | 97.2645 | 97.6594 | 97.7318 | 97.7681
Fronius International GmbH | Fronius Symo 22.7-3 480 | PV Inverter | 500 | 720 | 800 | 480 | 22.73 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-22.7-3-480-480V | Y | 1.03 | 2.27 | 4.55 | 6.82 | 11.36 | 17.05 | 22.73 | 94.3 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.4 | 97.6 | 97.8 | 98 | 98 | 98 | 95.9 | 97.3 | 97.7 | 97.8 | 97.9 | 97.8
Fronius International GmbH | Fronius Symo Advanced 22.7-3 480 | PV Inverter | 500 | 722 | 800 | 480 | 22.876 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-22.7-3-480-480V | Y | 1 | 2.2876 | 4.5752 | 6.8627 | 11.4379 | 17.1568 | 22.8758 | 94.3192 | 96.1631 | 96.6618 | 96.9515 | 96.9908 | 96.9484 | 96.3886 | 97.5518 | 97.8068 | 97.9996 | 98.0209 | 97.9813 | 95.9441 | 97.3371 | 97.6666 | 97.8392 | 97.8629 | 97.8067
Fronius International GmbH | Fronius Symo Advanced 22.7-3 480 Lite | PV Inverter | 500 | 722 | 800 | 480 | 22.876 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-22.7-3-480-Lite-480V | Y | 1 | 2.2876 | 4.5752 | 6.8627 | 11.4379 | 17.1568 | 22.8758 | 94.3192 | 96.1631 | 96.6618 | 96.9515 | 96.9908 | 96.9484 | 96.3886 | 97.5518 | 97.8068 | 97.9996 | 98.0209 | 97.9813 | 95.9441 | 97.3371 | 97.6666 | 97.8392 | 97.8629 | 97.8067
Fronius International GmbH | Fronius Symo 24.0-3 480 | PV Inverter | 500 | 725 | 800 | 480 | 24 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-24.0-3-480-480V | Y | 1.03 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 94.3 | 96.1 | 96.6 | 97 | 97 | 97 | 96.2 | 97.5 | 97.8 | 98 | 98 | 97.9 | 95.8 | 97.2 | 97.6 | 97.8 | 97.8 | 97.7
Fronius International GmbH | Fronius Symo Advanced 24.0-3 480 | PV Inverter | 500 | 722 | 800 | 480 | 24.142 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-24.0-3-480-480V | Y | 1 | 2.4142 | 4.8284 | 7.2425 | 12.0709 | 18.1063 | 24.1418 | 94.2986 | 96.1383 | 96.5889 | 96.9511 | 96.9529 | 96.9541 | 96.245 | 97.4769 | 97.7906 | 97.9573 | 97.9828 | 97.923 | 95.7696 | 97.2344 | 97.6169 | 97.8217 | 97.8136 | 97.7248
Fronius International GmbH | Fronius Symo Advanced 24.0-3 480 Lite | PV Inverter | 500 | 722 | 800 | 480 | 24.142 | CEC Inverter Database | 480V | Fronius-International-GmbH-Fronius-Symo-Advanced-24.0-3-480-Lite-480V | Y | 1 | 2.4142 | 4.8284 | 7.2425 | 12.0709 | 18.1063 | 24.1418 | 94.2986 | 96.1383 | 96.5889 | 96.9511 | 96.9529 | 96.9541 | 96.245 | 97.4769 | 97.7906 | 97.9573 | 97.9828 | 97.923 | 95.7696 | 97.2344 | 97.6169 | 97.8217 | 97.8136 | 97.7248
Gamesa Electric | PV3800 | PV Inverter | 835 | 1050 | 1300 | 600 | 3418.394 | CEC Inverter Database | 600V | Gamesa-Electric-PV3800-600V | Y | 267 | 341.8394 | 683.6788 | 1025.5182 | 1709.197 | 2563.7955 | 3418.394 | 97.5368 | 98.6736 | 98.6896 | 98.5623 | 98.2361 | 97.9035 | 96.8188 | 98.0047 | 98.478 | 98.2951 | 97.85 | 97.4265 | 95.972 | 97.5805 | 98.0808 | 98.0328 | 97.6733 | 97.2614
Gamesa Electric | PV4000 | PV Inverter | 875 | 1050 | 1300 | 630 | 3597.332 | CEC Inverter Database | 630V | Gamesa-Electric-PV4000-630V | Y | 267 | 359.7332 | 719.4664 | 1079.1996 | 1798.666 | 2697.999 | 3597.332 | 97.4581 | 98.5595 | 98.6972 | 98.5797 | 98.2482 | 97.9387 | 96.7477 | 98.0329 | 98.356 | 98.2625 | 97.8771 | 97.5187 | 96.2671 | 97.713 | 98.2326 | 98.1645 | 97.7513 | 97.3373
Gamesa Electric | PV4100 | PV Inverter | 835 | 1050 | 1300 | 600 | 3644.066 | CEC Inverter Database | 600V | Gamesa-Electric-PV4100-600V | Y | 267 | 364.4066 | 728.8132 | 1093.2198 | 1822.033 | 2733.0495 | 3644.066 | 97.6024 | 98.7445 | 98.7974 | 98.6028 | 98.2077 | 97.8843 | 96.8362 | 98.0652 | 98.588 | 98.0592 | 97.826 | 97.3341 | 95.8937 | 97.673 | 98.2694 | 98.146 | 97.6987 | 97.2756
Gamesa Electric | PV4200 | PV Inverter | 915 | 1050 | 1300 | 660 | 3767.352 | CEC Inverter Database | 660V | Gamesa-Electric-PV4200-660V | Y | 267 | 376.7352 | 753.4704 | 1130.2056 | 1883.676 | 2825.514 | 3767.352 | 97.4802 | 98.7142 | 98.8271 | 98.6953 | 98.3759 | 98.0193 | 96.9767 | 98.5407 | 98.7092 | 98.53 | 98.1361 | 97.7017 | 96.4716 | 97.7801 | 98.2885 | 98.221 | 97.9008 | 97.4865
Gamesa Electric | PV4300 | PV Inverter | 875 | 1050 | 1300 | 630 | 3826.652 | CEC Inverter Database | 630V | Gamesa-Electric-PV4300-630V | Y | 267 | 382.6652 | 765.3304 | 1147.9956 | 1913.326 | 2869.989 | 3826.652 | 97.572 | 98.6565 | 98.7953 | 98.6438 | 98.2843 | 97.9457 | 97.0358 | 98.4773 | 98.5621 | 98.3725 | 97.9356 | 97.4696 | 96.094 | 97.8374 | 98.3574 | 98.2203 | 97.7892 | 97.3192
Gamesa Electric | PV4400 | PV Inverter | 955 | 1050 | 1300 | 690 | 3939.574 | CEC Inverter Database | 690V | Gamesa-Electric-PV4400-690V | Y | 267 | 393.9574 | 787.9148 | 1181.8722 | 1969.787 | 2954.6805 | 3939.574 | 97.42 | 98.3506 | 98.6127 | 98.6011 | 98.3075 | 98.0508 | 96.9302 | 98.0124 | 98.3502 | 98.3186 | 97.9864 | 97.6293 | 96.0812 | 97.6626 | 97.9195 | 97.9842 | 97.6762 | 97.2743
Gamesa Electric | PV4500 | PV Inverter | 915 | 1050 | 1300 | 660 | 4006.946 | CEC Inverter Database | 660V | Gamesa-Electric-PV4500-660V | Y | 267 | 400.6946 | 801.3892 | 1202.0838 | 2003.473 | 3005.2095 | 4006.946 | 97.5099 | 98.7494 | 98.8289 | 98.6843 | 98.3181 | 98.0108 | 96.9982 | 98.5232 | 98.5734 | 98.433 | 98.0395 | 97.6204 | 96.4861 | 97.8213 | 98.4772 | 98.3072 | 97.8413 | 97.4256
Gamesa Electric | PV4700 | PV Inverter | 955 | 1050 | 1300 | 690 | 4190.43 | CEC Inverter Database | 690V | Gamesa-Electric-PV4700-690V | Y | 267 | 419.043 | 838.086 | 1257.129 | 2095.215 | 3142.8225 | 4190.43 | 97.4916 | 98.7995 | 98.8886 | 98.7326 | 98.3487 | 98.0507 | 97.1562 | 98.4764 | 98.583 | 98.4348 | 98.0743 | 97.6869 | 96.5244 | 97.9731 | 98.5074 | 98.4205 | 97.9383 | 97.5044
GE Renewable Energy | RIU-2500-U | PV Inverter | 800 | 975 | 1500 | 550 | 2507.194 | CEC Inverter Database | 550V | GE-Renewable-Energy-RIU-2500-U-550V | Y | 62.8 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426
Generac Power Systems | X7602 | PV Inverter | 390 | 400 | 420 | 240 | 7.586 | CEC Inverter Database | 240V | Generac-Power-Systems-X7602-240V | Y | 1.2917 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91
Generac Power Systems | XVT076A03 | PV Inverter | 390 | 400 | 420 | 240 | 7.839 | CEC Inverter Database | 240V | Generac-Power-Systems-XVT076A03-240V | Y | 1.29 | 0.78386 | 1.5677 | 2.3516 | 3.9193 | 5.879 | 7.8386 | 93.6776 | 95.9987 | 96.5326 | 97.2036 | 97.1603 | 97.1047 | 92.8234 | 95.6083 | 96.6681 | 97.2129 | 97.2231 | 97.1337 | 92.2887 | 95.332 | 96.1902 | 96.9866 | 97.13 | 97.0189
Generac Power Systems | X11402 | PV Inverter | 390 | 400 | 420 | 208 | 11.18 | CEC Inverter Database | 208V | Generac-Power-Systems-X11402-208V | Y | 0.125 | 1.118 | 2.236 | 3.354 | 5.59 | 8.385 | 11.18 | 97.25 | 97.35 | 97.58 | 97.65 | 97.44 | 97.06 | 97.03 | 97.35 | 97.67 | 97.54 | 97.25 | 96.93 | 95.83 | 97.24 | 97.27 | 97.39 | 97.08 | 96.89
Generac Power Systems | XVT114G03 | PV Inverter | 390 | 400 | 420 | 208 | 11.748 | CEC Inverter Database | 208V | Generac-Power-Systems-XVT114G03-208V | Y | 0.13 | 1.1748 | 2.3496 | 3.5243 | 5.8739 | 8.8109 | 11.7478 | 94.3952 | 96.3614 | 96.9844 | 97.3488 | 97.3913 | 97.3223 | 93.8375 | 96.116 | 96.8135 | 97.3003 | 97.2556 | 97.1149 | 92.9035 | 95.7659 | 96.54 | 97.0771 | 97.168 | 97.0658
Ginlong Technologies Co., Ltd. | Solis-1P2.5K-4G-US | PV Inverter | 120 | 330 | 500 | 240 | 2.5 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P2.5K-4G-US-240V | Y | 3.2 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.6401 | 94.6457 | 95.692 | 96.8363 | 96.713 | 96.4833 | 93.9159 | 95.5043 | 96.5921 | 97.6896 | 97.4379 | 97.114 | 93.7984 | 95.1685 | 96.3297 | 97.4269 | 96.9989 | 96.8047
Ginlong Technologies Co., Ltd. | Solis-1P3K-4G-US | PV Inverter | 140 | 330 | 500 | 240 | 3 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P3K-4G-US-240V | Y | 3.3 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8664 | 94.7136 | 95.6114 | 97.0574 | 96.8122 | 96.477 | 94.0667 | 95.6697 | 96.5539 | 97.7675 | 97.4264 | 97.0012 | 93.845 | 95.2969 | 96.1758 | 97.4408 | 97.1733 | 96.697
Ginlong Technologies Co., Ltd. | Solis-1P3.6K-4G-US | PV Inverter | 180 | 330 | 500 | 240 | 3.6 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P3.6K-4G-US-240V | Y | 3.5 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 93.8804 | 94.7446 | 95.6302 | 97.0904 | 96.8386 | 96.4907 | 93.9017 | 95.6722 | 96.8973 | 97.7959 | 97.4214 | 97.0622 | 93.8792 | 95.4947 | 96.5522 | 97.4831 | 97.1511 | 96.7645
Ginlong Technologies Co., Ltd. | Solis-1P4K-4G-US | PV Inverter | 190 | 330 | 500 | 240 | 4 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P4K-4G-US-240V | Y | 3.5 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8715 | 94.7255 | 96.0908 | 97.0869 | 96.8217 | 96.404 | 94.0293 | 95.7206 | 96.9837 | 97.9192 | 97.4909 | 97.3216 | 93.8761 | 95.4725 | 96.5568 | 97.5311 | 97.1444 | 96.7796
Ginlong Technologies Co., Ltd. | Solis-1P4.6K-4G-US | PV Inverter | 200 | 360 | 500 | 240 | 4.6 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P4.6K-4G-US-240V | Y | 3.6 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.0282 | 94.3391 | 95.7359 | 96.9043 | 96.8001 | 96.5325 | 94.0655 | 95.5741 | 96.9074 | 97.9375 | 97.5427 | 97.3118 | 93.7876 | 95.1009 | 96.5461 | 97.4374 | 97.2666 | 96.964
Ginlong Technologies Co., Ltd. | Solis-1P5K-4G-US | PV Inverter | 240 | 360 | 500 | 240 | 5 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P5K-4G-US-240V | Y | 3.6 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.9967 | 94.5979 | 95.7172 | 97.3161 | 97.0155 | 96.5167 | 94.5418 | 95.7374 | 96.5953 | 97.9319 | 97.6168 | 97.433 | 94.0094 | 94.9752 | 96.145 | 97.4705 | 97.3308 | 96.8481
Ginlong Technologies Co., Ltd. | RHI-1P5K-HVES-5G | PV Inverter | 115 | 330 | 450 | 240 | 5.003 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P5K-HVES-5G-240V | Y | 1 | 0.5 | 1.001 | 1.501 | 2.501 | 3.752 | 5.003 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | Solis-1P6K2-4G-US | PV Inverter | 300 | 360 | 500 | 240 | 6 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P6K2-4G-US-240V | Y | 3.5 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1975 | 94.8034 | 95.9161 | 97.4325 | 97.2123 | 96.7122 | 94.4335 | 95.6416 | 96.5269 | 97.8303 | 97.7139 | 97.3363 | 94.2126 | 95.1763 | 96.3489 | 97.6663 | 97.5266 | 97.0427
Ginlong Technologies Co., Ltd. | Solis-1P6K-4G-US | PV Inverter | 200 | 380 | 500 | 240 | 6 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P6K-4G-US-240V | Y | 6 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.8998 | 96.1208 | 96.7645 | 97.3045 | 97.3234 | 96.4761 | 95.5487 | 96.9813 | 97.3964 | 97.4228 | 97.3717 | 97.9525 | 95.3083 | 96.9146 | 97.4794 | 97.5873 | 97.5795 | 97.5828
Ginlong Technologies Co., Ltd. | RHI-1P6K-HVES-5G | PV Inverter | 130 | 330 | 450 | 240 | 6.004 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P6K-HVES-5G-240V | Y | 1 | 0.6 | 1.201 | 1.801 | 3.002 | 4.503 | 6.004 | 94.9 | 96.12 | 96.76 | 97.3 | 97.32 | 96.48 | 95.55 | 96.98 | 97.4 | 97.42 | 97.37 | 97.95 | 95.31 | 96.91 | 97.48 | 97.59 | 97.58 | 97.58
Ginlong Technologies Co., Ltd. | Solis-1P7K-4G-US | PV Inverter | 250 | 380 | 500 | 240 | 7 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P7K-4G-US-240V | Y | 7 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94.9607 | 96.155 | 96.8314 | 97.3565 | 97.3538 | 96.5398 | 95.5846 | 97.0123 | 97.429 | 97.5 | 97.509 | 97.0437 | 95.3208 | 96.9551 | 97.5201 | 97.6639 | 97.5988 | 97.5959
Ginlong Technologies Co., Ltd. | RHI-1P7K-HVES-5G | PV Inverter | 160 | 330 | 450 | 240 | 7.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P7K-HVES-5G-240V | Y | 1 | 0.701 | 1.401 | 2.102 | 3.503 | 5.254 | 7.006 | 94.96 | 96.16 | 96.83 | 97.36 | 97.35 | 96.54 | 95.58 | 97.01 | 97.43 | 97.5 | 97.51 | 97.04 | 95.32 | 96.96 | 97.52 | 97.66 | 97.6 | 97.6
Ginlong Technologies Co., Ltd. | Solis-1P7.6K-4G-US | PV Inverter | 200 | 380 | 500 | 240 | 7.6 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P7.6K-4G-US-240V | Y | 7 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.0545 | 96.1601 | 96.8885 | 97.3433 | 97.1468 | 96.576 | 95.631 | 97.1836 | 97.4753 | 97.7794 | 97.347 | 97.8962 | 95.3586 | 96.7534 | 97.606 | 97.8242 | 97.8541 | 97.7094
Ginlong Technologies Co., Ltd. | RHI-1P7.6K-HVES-5G | PV Inverter | 175 | 330 | 450 | 240 | 7.603 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P7.6K-HVES-5G-240V | Y | 1 | 0.76 | 1.521 | 2.281 | 3.801 | 5.702 | 7.603 | 95.05 | 96.16 | 96.89 | 97.34 | 97.15 | 96.58 | 95.63 | 97.18 | 97.48 | 97.78 | 97.35 | 97.9 | 95.36 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | Solis-1P8K-4G-US | PV Inverter | 250 | 380 | 500 | 240 | 8 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P8K-4G-US-240V | Y | 6 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1153 | 96.1755 | 96.939 | 97.3693 | 97.1827 | 96.6319 | 95.6565 | 97.2399 | 97.4217 | 97.5479 | 97.7024 | 96.9559 | 95.3757 | 96.7466 | 97.6107 | 97.8173 | 97.8528 | 97.7053
Ginlong Technologies Co., Ltd. | RHI-1P8K-HVES-5G | PV Inverter | 185 | 330 | 450 | 240 | 8.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P8K-HVES-5G-240V | Y | 1 | 0.801 | 1.601 | 2.402 | 4.003 | 6.004 | 8.006 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | Solis-1P9K-4G-US | PV Inverter | 250 | 380 | 500 | 240 | 9 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P9K-4G-US-240V | Y | 7 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.142 | 96.7533 | 96.9992 | 97.4866 | 97.373 | 96.9957 | 95.718 | 97.2744 | 97.4478 | 97.6088 | 97.7501 | 97.1064 | 95.5774 | 96.7392 | 97.6611 | 97.8213 | 97.8215 | 97.7076
Ginlong Technologies Co., Ltd. | RHI-1P9K-HVES-5G | PV Inverter | 210 | 330 | 450 | 240 | 9.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P9K-HVES-5G-240V | Y | 1 | 0.901 | 1.801 | 2.702 | 4.503 | 6.754 | 9.006 | 95.14 | 96.75 | 97 | 97.49 | 97.37 | 97 | 95.72 | 97.27 | 97.45 | 97.61 | 97.75 | 97.11 | 95.58 | 96.74 | 97.66 | 97.82 | 97.82 | 97.71
Ginlong Technologies Co., Ltd. | Solis-1P10K-4G-US | PV Inverter | 250 | 380 | 500 | 240 | 10 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-Solis-1P10K-4G-US-240V | Y | 7 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.2 | 96.8 | 97.1 | 97.5 | 97.6 | 97.1 | 95.3 | 96.3 | 97.6 | 97.7 | 97.7 | 97.2 | 95.6 | 96.8 | 97.7 | 97.8 | 97.8 | 97.7
Ginlong Technologies Co., Ltd. | RHI-1P10K-HVES-5G | PV Inverter | 230 | 330 | 450 | 240 | 10.005 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P10K-HVES-5G-240V | Y | 1 | 1 | 2.001 | 3.001 | 5.002 | 7.504 | 10.005 | 95.18 | 96.78 | 97.08 | 97.55 | 97.61 | 97.06 | 95.3 | 96.32 | 97.58 | 97.66 | 97.73 | 97.21 | 95.6 | 96.8 | 97.68 | 97.79 | 97.81 | 97.71
Ginlong Technologies Co., Ltd. | Solis-25K-US-LSW | PV Inverter | 347 | 470 | 800 | 480 | 24.958 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-25K-US-LSW-480V | Y | 1 | 2.4958 | 4.9916 | 7.4874 | 12.479 | 18.7185 | 24.9581 | 97.8538 | 98.3868 | 98.42 | 98.5665 | 98.4105 | 98.354 | 98.0001 | 98.4275 | 98.4174 | 98.6659 | 98.423 | 98.3476 | 97.893 | 98.4187 | 98.493 | 98.685 | 98.4659 | 98.373
Ginlong Technologies Co., Ltd. | Solis-25K-US | PV Inverter | 580 | 650 | 780 | 480 | 25 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-25K-US-480V | Y | 14 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5
Ginlong Technologies Co., Ltd. | Solis-25K-US-SW | PV Inverter | 580 | 650 | 770 | 480 | 25 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-25K-US-SW-480V | Y | 14 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.143 | 97.3103 | 97.5582 | 97.902 | 98.1863 | 97.7856 | 97.1369 | 97.2947 | 97.4013 | 97.8837 | 98.2954 | 97.7509 | 97.2361 | 97.396 | 97.5435 | 97.6922 | 98.0012 | 97.4855
Ginlong Technologies Co., Ltd. | Solis-30K-US-LSW | PV Inverter | 417 | 700 | 800 | 480 | 29.948 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-30K-US-LSW-480V | Y | 1 | 2.9948 | 5.9895 | 8.9843 | 14.9738 | 22.4607 | 29.9477 | 97.7689 | 98.392 | 98.4344 | 98.5669 | 98.4121 | 98.3166 | 97.814 | 98.4242 | 98.504 | 98.651 | 98.42 | 98.356 | 97.89 | 98.4279 | 98.517 | 98.6982 | 98.451 | 98.365
Ginlong Technologies Co., Ltd. | Solis-30K-US | PV Inverter | 580 | 650 | 780 | 480 | 30 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-30K-US-480V | Y | 15 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8
Ginlong Technologies Co., Ltd. | Solis-30K-US-SW | PV Inverter | 580 | 650 | 780 | 480 | 30 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-30K-US-SW-480V | Y | 15 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1367 | 97.9124 | 97.905 | 98.3089 | 97.8705 | 97.9174 | 97.3783 | 98.0388 | 98.0359 | 98.3477 | 98.1139 | 97.915 | 97.12 | 97.8656 | 97.9617 | 98.2389 | 97.9687 | 97.8103
Ginlong Technologies Co., Ltd. | Solis-36K-US-LSW | PV Inverter | 500 | 700 | 800 | 480 | 35.925 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-36K-US-LSW-480V | Y | 1 | 3.5925 | 7.185 | 10.7775 | 17.9625 | 26.9438 | 35.9251 | 97.7435 | 98.365 | 98.4061 | 98.579 | 98.4309 | 98.3073 | 97.796 | 98.3474 | 98.465 | 98.636 | 98.468 | 98.334 | 97.826 | 98.4038 | 98.496 | 98.6621 | 98.483 | 98.319
Ginlong Technologies Co., Ltd. | Solis-36K-US | PV Inverter | 580 | 650 | 780 | 480 | 36 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-36K-US-480V | Y | 15 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1
Ginlong Technologies Co., Ltd. | Solis-36K-US-F-SW | PV Inverter | 580 | 650 | 780 | 480 | 36 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-36K-US-F-SW-480V | Y | 15 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3526 | 98.1527 | 98.1207 | 98.3457 | 98.0251 | 98.1578 | 97.6373 | 98.3239 | 98.2591 | 98.4238 | 98.3573 | 98.1446 | 97.3742 | 98.154 | 98.2089 | 98.3757 | 98.1704 | 98.0833
Ginlong Technologies Co., Ltd. | Solis-36K-US-SW | PV Inverter | 580 | 650 | 780 | 480 | 36 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-36K-US-SW-480V | Y | 15 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3556 | 98.1469 | 98.1132 | 98.3457 | 98.0215 | 98.1483 | 97.6545 | 98.3164 | 98.2591 | 98.438 | 98.343 | 98.1379 | 97.3624 | 98.154 | 98.2138 | 98.3749 | 98.1715 | 98.0758
Ginlong Technologies Co., Ltd. | Solis-40K-US-LSW | PV Inverter | 556 | 700 | 800 | 480 | 39.926 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-40K-US-LSW-480V | Y | 1 | 3.9926 | 7.9852 | 11.9778 | 19.9629 | 29.9444 | 39.9259 | 97.7566 | 98.3499 | 98.431 | 98.5651 | 98.4319 | 98.3273 | 97.787 | 98.3669 | 98.459 | 98.628 | 98.441 | 98.347 | 97.832 | 98.4148 | 98.466 | 98.635 | 98.515 | 98.336
Ginlong Technologies Co., Ltd. | Solis-40K-US | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-40K-US-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2
Ginlong Technologies Co., Ltd. | Solis-40K-US-F | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-40K-US-F-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98
Ginlong Technologies Co., Ltd. | Solis-40K-US-F-SW | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-40K-US-F-SW-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.47 | 98.0068 | 98.0574 | 98.1972 | 98.114 | 98.0292 | 97.9259 | 98.3089 | 98.392 | 98.7145 | 98.5725 | 98.3423 | 97.5823 | 98.1565 | 98.1932 | 98.4353 | 98.3489 | 98.2444
Ginlong Technologies Co., Ltd. | Solis-40K-US-SW | PV Inverter | 580 | 650 | 780 | 480 | 40 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-40K-US-SW-480V | Y | 1 | 4 | 8 | 12 | 20 | 30 | 40 | 97.4777 | 98.0039 | 98.0564 | 98.1952 | 98.1258 | 98.0274 | 97.9247 | 98.3105 | 98.4002 | 98.7211 | 98.5785 | 98.342 | 97.5764 | 98.1504 | 98.1795 | 98.4337 | 98.3428 | 98.244
Ginlong Technologies Co., Ltd. | Solis-50K-US-F-LSW | PV Inverter | 568 | 720 | 850 | 480 | 49.916 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-F-LSW-480V | Y | 1 | 4.9916 | 9.9832 | 14.9748 | 24.9581 | 37.4371 | 49.9161 | 97.752 | 98.3642 | 98.434 | 98.585 | 98.42 | 98.313 | 97.791 | 98.3809 | 98.447 | 98.645 | 98.443 | 98.352 | 97.84 | 98.411 | 98.483 | 98.68 | 98.493 | 98.3201
Ginlong Technologies Co., Ltd. | Solis-50K-US-LSW | PV Inverter | 568 | 720 | 850 | 480 | 49.984 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-LSW-480V | Y | 1 | 4.9984 | 9.9967 | 14.9951 | 24.9918 | 37.4877 | 49.9837 | 97.743 | 98.3898 | 98.433 | 98.553 | 98.436 | 98.35 | 97.794 | 98.358 | 98.449 | 98.655 | 98.437 | 98.31 | 97.8057 | 98.4135 | 98.478 | 98.721 | 98.474 | 98.359
Ginlong Technologies Co., Ltd. | Solis-50K-US | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5
Ginlong Technologies Co., Ltd. | Solis-50K-US-F | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-F-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.74 | 98.44 | 98.46 | 98.58 | 98.45 | 98.35 | 97.8 | 98.53 | 98.55 | 98.7 | 98.51 | 98.4 | 97.88 | 98.58 | 98.65 | 98.76 | 98.57 | 98.46
Ginlong Technologies Co., Ltd. | Solis-50K-US-F-SW | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-F-SW-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644
Ginlong Technologies Co., Ltd. | Solis-50K-US-SW | PV Inverter | 580 | 650 | 720 | 480 | 50 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-50K-US-SW-480V | Y | 1 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006
Ginlong Technologies Co., Ltd. | Solis-60K-US-F-LSW | PV Inverter | 526 | 720 | 850 | 480 | 59.933 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-60K-US-F-LSW-480V | Y | 1 | 5.9933 | 11.9866 | 17.9798 | 29.9664 | 44.9496 | 59.9328 | 97.739 | 98.411 | 98.444 | 98.579 | 98.412 | 98.28 | 97.787 | 98.4024 | 98.465 | 98.622 | 98.441 | 98.342 | 97.809 | 98.434 | 98.522 | 98.689 | 98.48 | 98.326
Ginlong Technologies Co., Ltd. | Solis-60K-US-F | PV Inverter | 580 | 650 | 720 | 480 | 60 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-60K-US-F-480V | Y | 1 | 6 | 12 | 18 | 30 | 45 | 60 | 97.73 | 98.31 | 98.42 | 98.55 | 98.37 | 98.22 | 97.82 | 98.45 | 98.54 | 98.63 | 98.5 | 98.33 | 97.86 | 98.53 | 98.59 | 98.7 | 98.55 | 98.45
Ginlong Technologies Co., Ltd. | Solis-60K-US-F-SW | PV Inverter | 580 | 650 | 720 | 480 | 60 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-60K-US-F-SW-480V | Y | 1 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499
Ginlong Technologies Co., Ltd. | Solis-66K-US-F-LSW | PV Inverter | 579 | 720 | 850 | 480 | 65.926 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-66K-US-F-LSW-480V | Y | 1 | 6.5926 | 13.1851 | 19.7777 | 32.9628 | 49.4441 | 65.9255 | 97.752 | 98.351 | 98.413 | 98.588 | 98.42 | 98.31 | 97.773 | 98.343 | 98.48 | 98.677 | 98.436 | 98.319 | 97.807 | 98.369 | 98.501 | 98.657 | 98.487 | 98.321
Ginlong Technologies Co., Ltd. | Solis-66K-US-F | PV Inverter | 580 | 650 | 720 | 480 | 66 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-66K-US-F-480V | Y | 1 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.57 | 98.38 | 98.48 | 98.56 | 98.42 | 98.31 | 97.74 | 98.5 | 98.55 | 98.7 | 98.5 | 98.39 | 97.77 | 98.67 | 98.65 | 98.77 | 98.56 | 98.49
Ginlong Technologies Co., Ltd. | Solis-66K-US-F-SW | PV Inverter | 580 | 650 | 720 | 480 | 66 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-66K-US-F-SW-480V | Y | 1 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918
Ginlong Technologies Co., Ltd. | Solis-75K-5G-US | PV Inverter | 550 | 720 | 850 | 480 | 75 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-75K-5G-US-480V | Y | 1 | 7.5002 | 15.0005 | 22.5007 | 37.5012 | 56.2517 | 75.0023 | 98.147 | 98.5383 | 98.525 | 98.6238 | 98.3792 | 98.2162 | 98.1775 | 98.5215 | 98.5439 | 98.6666 | 98.4445 | 98.2384 | 98.244 | 98.5737 | 99.0148 | 98.6211 | 98.5743 | 98.294
Ginlong Technologies Co., Ltd. | Solis-80K-5G-US | PV Inverter | 550 | 720 | 850 | 480 | 80 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-80K-5G-US-480V | Y | 1 | 8.0003 | 16.0006 | 24.0009 | 40.0015 | 60.0023 | 80.0031 | 98.1441 | 98.5363 | 98.5241 | 98.6265 | 98.3794 | 98.2123 | 98.1764 | 98.5232 | 98.543 | 98.6654 | 98.4447 | 98.2424 | 98.2451 | 98.5776 | 99.0149 | 98.6271 | 98.575 | 98.2898
Ginlong Technologies Co., Ltd. | Solis-90K-5G-US | PV Inverter | 550 | 720 | 850 | 480 | 90 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-90K-5G-US-480V | Y | 1 | 9.0005 | 18.001 | 27.0015 | 45.0024 | 67.5036 | 90.0049 | 98.1425 | 98.5301 | 98.5175 | 98.6202 | 98.382 | 98.2129 | 98.1677 | 98.5208 | 98.5367 | 98.6571 | 98.4429 | 98.2296 | 98.24 | 98.5713 | 99.0158 | 98.6197 | 98.5715 | 98.2914
Ginlong Technologies Co., Ltd. | Solis-100K-5G-US | PV Inverter | 550 | 720 | 850 | 480 | 100 | CEC Inverter Database | 480V | Ginlong-Technologies-Co.,-Ltd.-Solis-100K-5G-US-480V | Y | 1 | 10.0004 | 20.0008 | 30.0012 | 50.002 | 75.003 | 100.004 | 98.1406 | 98.5261 | 98.5197 | 98.6189 | 98.3796 | 98.2109 | 98.1693 | 98.5244 | 98.5388 | 98.6582 | 98.442 | 98.2301 | 98.242 | 98.5714 | 99.0139 | 98.6188 | 98.571 | 98.2889
Ginlong Technologies Co., Ltd. | Solis-100K-EHV-5G | PV Inverter | 860 | 950 | 1250 | 600 | 100 | CEC Inverter Database | 600V | Ginlong-Technologies-Co.,-Ltd.-Solis-100K-EHV-5G-600V | Y | 1 | 10.0084 | 20.0168 | 30.0251 | 50.0419 | 75.0628 | 100.0838 | 98.9662 | 99.0442 | 98.8859 | 98.9722 | 98.9 | 98.6475 | 98.5983 | 98.7913 | 98.8721 | 98.8004 | 98.6123 | 98.636 | 98.2767 | 98.6281 | 98.6406 | 98.6296 | 98.4678 | 98.2644
Ginlong Technologies Co., Ltd. | Solis-125K-EHV-5G | PV Inverter | 860 | 950 | 1250 | 600 | 125 | CEC Inverter Database | 600V | Ginlong-Technologies-Co.,-Ltd.-Solis-125K-EHV-5G-600V | Y | 1 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.9167 | 99.0279 | 98.941 | 98.9462 | 98.8521 | 98.7464 | 98.5469 | 98.8405 | 98.7722 | 98.8039 | 98.6338 | 98.6288 | 98.2805 | 98.7 | 98.7947 | 98.6619 | 98.4679 | 98.3006
Ginlong Technologies Co., Ltd. | Solis-125K1-EHV-5G | PV Inverter | 860 | 1080 | 1250 | 600 | 125.083 | CEC Inverter Database | 600V | Ginlong-Technologies-Co.,-Ltd.-Solis-125K1-EHV-5G-600V | Y | 1 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.2442 | 98.6339 | 98.622 | 98.725 | 98.4773 | 98.3136 | 98.2735 | 98.6299 | 98.6462 | 98.7609 | 98.5469 | 98.336 | 98.3436 | 98.6734 | 99.1159 | 98.7211 | 98.6759 | 98.3966
Ginlong Technologies Co., Ltd. | Solis-185K-EHV-5G-US | PV Inverter | 850 | 1080 | 1300 | 600 | 185.005 | CEC Inverter Database | 600V | Ginlong-Technologies-Co.,-Ltd.-Solis-185K-EHV-5G-US-600V | Y | 1 | 18.5005 | 37.0011 | 55.5016 | 92.5026 | 138.7539 | 185.0053 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 97.932 | 98.566 | 98.654 | 98.582 | 98.404 | 98.181 | 97.65 | 98.488 | 98.579 | 98.893 | 98.698 | 98.444
Ginlong Technologies Co., Ltd. | Solis-255K-EHV-5G-US | PV Inverter | 850 | 1080 | 1300 | 800 | 255.013 | CEC Inverter Database | 800V | Ginlong-Technologies-Co.,-Ltd.-Solis-255K-EHV-5G-US-800V | Y | 1 | 25.5013 | 51.0025 | 76.5038 | 127.5063 | 191.2595 | 255.0126 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 97.645 | 98.299 | 98.495 | 98.546 | 98.427 | 98.255 | 98.059 | 98.701 | 98.84 | 98.835 | 98.696 | 98.521
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/AC 340 | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-Q.PEAK-DUO-BLK-G6+-AC-340-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/AC 345 | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-Q.PEAK-DUO-BLK-G6+-AC-345-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-6.0 | PV Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-6.0-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-7.0 | PV Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-7.0-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-7.6 | PV Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-7.6-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-8.6 | PV Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-8.6-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
HiQ Solar | TSXL480-10k | PV Inverter | 450 | 750 | 850 | 480 | 9.975 | CEC Inverter Database | 480V | HiQ-Solar-TSXL480-10k-480V | Y | 8.3 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2
Hoymiles Power Electronics Inc. | HM-300N | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-300N-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HM-300NA | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-300NA-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HM-300NT | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-300NT-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HMS-300-1A-NA | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-300-1A-NA-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HMS-300-1D-NA | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-300-1D-NA-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HMS-300-1T-NA | PV Inverter | 29 | 40 | 48 | 240 | 0.29542 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-300-1T-NA-240V | Y | 0.108 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541
Hoymiles Power Electronics Inc. | HM-350N | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-350N-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HM-350NA | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-350NA-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HM-350NT | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-350NT-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HMS-350-1A-NA | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-350-1A-NA-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HMS-350-1D-NA | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-350-1D-NA-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HMS-350-1T-NA | PV Inverter | 33 | 40 | 48 | 240 | 0.3495 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-350-1T-NA-240V | Y | 0.105 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412
Hoymiles Power Electronics Inc. | HM-400N | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-400N-240V | Y | 0.105 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089
Hoymiles Power Electronics Inc. | HM-400NA | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-400NA-240V | Y | 0.105 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089
Hoymiles Power Electronics Inc. | HM-400NT | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-400NT-240V | Y | 0.105 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089
Hoymiles Power Electronics Inc. | HMS-400-1A-NA | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-400-1A-NA-240V | Y | 0.105 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 95.23 | 96.22 | 96.26 | 96.55 | 96.78 | 96.19 | 95.68 | 96.13 | 96.41 | 96.34 | 96.78 | 96.53 | 96.04 | 95.97 | 96.41 | 96.2 | 96.7 | 96.61
Hoymiles Power Electronics Inc. | HMS-400-1D-NA | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-400-1D-NA-240V | Y | 0.105 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 95.23 | 96.22 | 96.26 | 96.55 | 96.78 | 96.19 | 95.68 | 96.13 | 96.41 | 96.34 | 96.78 | 96.53 | 96.04 | 95.97 | 96.41 | 96.2 | 96.7 | 96.61
Hoymiles Power Electronics Inc. | HMS-400-1T-NA | PV Inverter | 34 | 42 | 48 | 240 | 0.38254 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-400-1T-NA-240V | Y | 0.105 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 95.23 | 96.22 | 96.26 | 96.55 | 96.78 | 96.19 | 95.68 | 96.13 | 96.41 | 96.34 | 96.78 | 96.53 | 96.04 | 95.97 | 96.41 | 96.2 | 96.7 | 96.61
Hoymiles Power Electronics Inc. | HM-600N | PV Inverter | 29 | 37 | 48 | 240 | 0.591 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-600N-240V | Y | 0.11 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756
Hoymiles Power Electronics Inc. | HM-600NT | PV Inverter | 29 | 37 | 48 | 240 | 0.591 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-600NT-240V | Y | 0.11 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756
Hoymiles Power Electronics Inc. | HMS-600-2D-NA | PV Inverter | 29 | 37 | 48 | 240 | 0.591 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-600-2D-NA-240V | Y | 0.11 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756
Hoymiles Power Electronics Inc. | HMS-600-2T-NA | PV Inverter | 29 | 37 | 48 | 240 | 0.591 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-600-2T-NA-240V | Y | 0.11 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756
Hoymiles Power Electronics Inc. | HM-700N | PV Inverter | 33 | 42 | 48 | 240 | 0.697 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-700N-240V | Y | 0.11 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753
Hoymiles Power Electronics Inc. | HM-700NT | PV Inverter | 33 | 42 | 48 | 240 | 0.697 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-700NT-240V | Y | 0.11 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753
Hoymiles Power Electronics Inc. | HMS-700-2D-NA | PV Inverter | 33 | 42 | 48 | 240 | 0.697 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-700-2D-NA-240V | Y | 0.11 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753
Hoymiles Power Electronics Inc. | HMS-700-2T-NA | PV Inverter | 33 | 42 | 48 | 240 | 0.697 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-700-2T-NA-240V | Y | 0.11 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753
Hoymiles Power Electronics Inc. | HM-800N | PV Inverter | 34 | 42 | 48 | 240 | 0.767 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-800N-240V | Y | 0.11 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575
Hoymiles Power Electronics Inc. | HM-800NT | PV Inverter | 34 | 42 | 48 | 240 | 0.767 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-800NT-240V | Y | 0.11 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575
Hoymiles Power Electronics Inc. | HMS-800-2D-NA | PV Inverter | 34 | 42 | 48 | 240 | 0.767 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-800-2D-NA-240V | Y | 0.11 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575
Hoymiles Power Electronics Inc. | HMS-800-2T-NA | PV Inverter | 34 | 42 | 48 | 240 | 0.767 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-800-2T-NA-240V | Y | 0.11 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575
Hoymiles Power Electronics Inc. | HM-1000N | PV Inverter | 32 | 40 | 48 | 240 | 0.985 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1000N-240V | Y | 0.11 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455
Hoymiles Power Electronics Inc. | HM-1000NT | PV Inverter | 32 | 40 | 48 | 240 | 0.985 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1000NT-240V | Y | 0.11 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455
Hoymiles Power Electronics Inc. | HMS-1000-4D-NA | PV Inverter | 32 | 40 | 48 | 240 | 0.985 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1000-4D-NA-240V | Y | 0.11 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455
Hoymiles Power Electronics Inc. | HMS-1000-4T-NA | PV Inverter | 32 | 40 | 48 | 240 | 0.985 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1000-4T-NA-240V | Y | 0.11 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455
Hoymiles Power Electronics Inc. | HM-1000 | PV Inverter | 27 | 37 | 48 | 240 | 1.032 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1000-240V | Y | 0.03 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125
Hoymiles Power Electronics Inc. | HM-1000T | PV Inverter | 27 | 37 | 48 | 240 | 1.032 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1000T-240V | Y | 0.03 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125
Hoymiles Power Electronics Inc. | HMS-1000-4D | PV Inverter | 27 | 37 | 48 | 240 | 1.032 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1000-4D-240V | Y | 0.03 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125
Hoymiles Power Electronics Inc. | HMS-1000-4T | PV Inverter | 27 | 37 | 48 | 240 | 1.032 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1000-4T-240V | Y | 0.03 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125
Hoymiles Power Electronics Inc. | HM-1200 | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1200-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HM-1200N | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1200N-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HM-1200NT | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1200NT-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HM-1200T | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1200T-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HMS-1200-4D | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1200-4D-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HMS-1200-4D-NA | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1200-4D-NA-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HMS-1200-4T | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1200-4T-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HMS-1200-4T-NA | PV Inverter | 32 | 40 | 48 | 240 | 1.213 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1200-4T-NA-240V | Y | 0.01461 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013
Hoymiles Power Electronics Inc. | HM-1500N | PV Inverter | 36 | 42 | 48 | 240 | 1.439 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1500N-240V | Y | 0.11 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755
Hoymiles Power Electronics Inc. | HM-1500NT | PV Inverter | 36 | 42 | 48 | 240 | 1.439 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1500NT-240V | Y | 0.11 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755
Hoymiles Power Electronics Inc. | HMS-1500-4D-NA | PV Inverter | 36 | 42 | 48 | 240 | 1.439 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1500-4D-NA-240V | Y | 0.11 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755
Hoymiles Power Electronics Inc. | HMS-1500-4T-NA | PV Inverter | 36 | 42 | 48 | 240 | 1.439 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1500-4T-NA-240V | Y | 0.11 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755
Hoymiles Power Electronics Inc. | HM-1500 | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1500-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
Hoymiles Power Electronics Inc. | HM-1500T | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HM-1500T-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
Hoymiles Power Electronics Inc. | HMS-1500-4D | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1500-4D-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
Hoymiles Power Electronics Inc. | HMS-1500-4T | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-HMS-1500-4T-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
Hoymiles Power Electronics Inc. | THM-1500 | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | Hoymiles-Power-Electronics-Inc.-THM-1500-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
Huawei Technologies Co., Ltd. | SUN2000-3.8KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 3.8 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-3.8KTL-USL0-240V | Y | 2.18 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 96.375 | 98.2332 | 98.6641 | 99.0028 | 99.0572 | 99.0776 | 96.1637 | 98.1176 | 98.4788 | 98.9469 | 99.0231 | 99.0365 | 96.0702 | 97.9945 | 98.4563 | 98.8641 | 98.9923 | 98.9967
Huawei Technologies Co., Ltd. | SUN2000-5KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 5 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-5KTL-USL0-240V | Y | 2.07 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 97.0703 | 98.3856 | 98.7211 | 99.0239 | 99.0199 | 98.8703 | 96.8811 | 98.3814 | 98.661 | 98.9319 | 98.966 | 98.8203 | 96.6926 | 98.2929 | 98.5924 | 98.8825 | 98.8862 | 98.7742
Huawei Technologies Co., Ltd. | SUN2000-7.6KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 7.6 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-7.6KTL-USL0-240V | Y | 2.06 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 98.0246 | 98.8109 | 98.9586 | 98.9973 | 98.9182 | 98.749 | 97.8253 | 98.7187 | 98.917 | 98.9382 | 98.8674 | 98.7164 | 97.6925 | 98.6266 | 98.8792 | 98.9113 | 98.8473 | 98.6766
Huawei Technologies Co., Ltd. | SUN2000-9KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 9 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-9KTL-USL0-240V | Y | 1.97 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 97.6847 | 98.6455 | 98.9199 | 99.0618 | 99.0359 | 98.9738 | 97.5338 | 98.5959 | 98.9052 | 99.0405 | 99.016 | 98.932 | 97.5773 | 98.5984 | 98.8583 | 99.0241 | 99.0091 | 98.9183
Huawei Technologies Co., Ltd. | SUN2000-10KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 10 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-10KTL-USL0-240V | Y | 1.98 | 1 | 2 | 3 | 5 | 7.5 | 10 | 97.6401 | 98.656 | 98.9366 | 99.0483 | 99.013 | 98.9033 | 97.4485 | 98.548 | 98.8594 | 99.0041 | 98.9773 | 98.8792 | 97.1851 | 98.4207 | 98.7677 | 98.933 | 98.9378 | 98.845
Huawei Technologies Co., Ltd. | SUN2000-11.4KTL-USL0 | PV Inverter | 370 | 395 | 420 | 240 | 11.4 | CEC Inverter Database | 240V | Huawei-Technologies-Co.,-Ltd.-SUN2000-11.4KTL-USL0-240V | Y | 1.97 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 97.8855 | 98.7855 | 98.9735 | 99.0471 | 98.9836 | 98.8375 | 97.7154 | 98.6539 | 98.9173 | 98.9881 | 98.9407 | 98.8014 | 97.5395 | 98.5822 | 98.8395 | 98.9436 | 98.9124 | 98.7749
Huawei Technologies Co., Ltd. | SUN2000-25KTL-US | PV Inverter | 560 | 730 | 800 | 480 | 25 | CEC Inverter Database | 480V | Huawei-Technologies-Co.,-Ltd.-SUN2000-25KTL-US-480V | Y | 1 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 95.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.9 | 96.3 | 97.7 | 98.2 | 98.4 | 98.4 | 98.4 | 95.9 | 97.5 | 98 | 98.3 | 98.3 | 98.3
Huawei Technologies Co., Ltd. | SUN2000-30KTL-US | PV Inverter | 560 | 730 | 800 | 480 | 30 | CEC Inverter Database | 480V | Huawei-Technologies-Co.,-Ltd.-SUN2000-30KTL-US-480V | Y | 1 | 3 | 6 | 9 | 15 | 22.5 | 30 | 96.1 | 97.4 | 97.7 | 97.9 | 97.9 | 97.8 | 96.6 | 97.9 | 98.3 | 98.4 | 98.4 | 98.3 | 96.4 | 97.8 | 98.2 | 98.3 | 98.3 | 98.2
Huawei Technologies Co., Ltd. | SUN2000-33KTL-US | PV Inverter | 460 | 720 | 850 | 480 | 33 | CEC Inverter Database | 480V | Huawei-Technologies-Co.,-Ltd.-SUN2000-33KTL-US-480V | Y | 1.8 | 3.3 | 6.6 | 9.9 | 16.5 | 24.75 | 33 | 95.6305 | 97.31 | 97.6239 | 97.8333 | 97.8889 | 97.7881 | 97.5169 | 98.6741 | 98.8513 | 98.8841 | 98.8741 | 98.7894 | 96.9145 | 98.1094 | 98.38 | 98.4576 | 98.4622 | 98.3838
Huawei Technologies Co., Ltd. | SUN2000-36KTL-US | PV Inverter | 490 | 720 | 850 | 480 | 36 | CEC Inverter Database | 480V | Huawei-Technologies-Co.,-Ltd.-SUN2000-36KTL-US-480V | Y | 1.8 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.4077 | 97.5458 | 97.8137 | 97.9912 | 97.9878 | 97.8775 | 97.9739 | 98.7413 | 98.8734 | 98.8955 | 98.8578 | 98.762 | 97.1101 | 98.2156 | 98.4158 | 98.4713 | 98.4443 | 98.3524
Huawei Technologies Co., Ltd. | SUN2000-40KTL-US | PV Inverter | 530 | 720 | 850 | 480 | 40 | CEC Inverter Database | 480V | Huawei-Technologies-Co.,-Ltd.-SUN2000-40KTL-US-480V | Y | 1.8 | 4 | 8 | 12 | 20 | 30 | 40 | 96.7485 | 97.7289 | 97.9466 | 98.102 | 98.049 | 97.9087 | 98.0538 | 98.7273 | 98.7781 | 98.8628 | 98.7907 | 98.8053 | 97.2662 | 98.2155 | 98.3638 | 98.4571 | 98.3764 | 98.4169
Huawei Technologies Co., Ltd. | SUN2000-45KTL-US-HV-D0 | PV Inverter | 800 | 1000 | 1200 | 600 | 45.207 | CEC Inverter Database | 600V | Huawei-Technologies-Co.,-Ltd.-SUN2000-45KTL-US-HV-D0-600V | Y | 1.11 | 4.5207 | 9.0414 | 13.5621 | 22.6035 | 33.9053 | 45.207 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.1 | 98.5 | 98.5 | 98.5 | 98.4 | 98.2 |  | Original power level values incorrectly set to efficiency values; replaced with calculated power levels from device rating
Huawei Technologies Co., Ltd. | SUN2000-100KTL-USH0 | PV Inverter | 880 | 1120 | 1200 | 800 | 100 | CEC Inverter Database | 800V | Huawei-Technologies-Co.,-Ltd.-SUN2000-100KTL-USH0-800V | Y | 2.61 | 10 | 20 | 30 | 50 | 75 | 100 | 97.2971 | 98.0491 | 98.3042 | 98.447 | 98.4104 | 98.3164 | 97.6913 | 98.412 | 98.5995 | 98.6923 | 98.6594 | 98.5739 | 98.2248 | 98.7907 | 98.9363 | 98.9879 | 98.9811 | 98.631
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 610TL U B220 | PV Inverter | 440 | 590 | 740 | 220 | 610 | CEC Inverter Database | 220V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-610TL-U-B220-220V | Y | 80 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 830TL U B300 | PV Inverter | 440 | 590 | 740 | 300 | 830 | CEC Inverter Database | 300V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-830TL-U-B300-300V | Y | 80 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 915TL U B330 | PV Inverter | 485 | 613 | 740 | 330 | 915 | CEC Inverter Database | 330V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-915TL-U-B330-330V | Y | 80 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1000TL U B360 | PV Inverter | 524 | 632 | 740 | 360 | 1000 | CEC Inverter Database | 360V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1000TL-U-B360-360V | Y | 80 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1140TL U B410 | PV Inverter | 595 | 668 | 800 | 410 | 1027.752 | CEC Inverter Database | 410V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1140TL-U-B410-410V | Y | 2550.2775 | 102.7752 | 205.5504 | 308.3256 | 513.876 | 770.814 | 1027.752 | 95.8625 | 97.4417 | 97.8113 | 97.8912 | 97.7441 | 97.3829 | 95.6736 | 97.3781 | 97.7557 | 97.8606 | 97.7193 | 97.3781 | 95.14 | 97.0801 | 97.524 | 97.6897 | 97.5561 | 97.213
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1245TL U B480 | PV Inverter | 697 | 949 | 1200 | 480 | 1042.22 | CEC Inverter Database | 480V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1245TL-U-B480-480V | Y | 459.0724 | 104.222 | 208.444 | 312.666 | 521.11 | 781.665 | 1042.22 | 96.9037 | 97.6188 | 97.803 | 97.7395 | 97.5015 | 97.1174 | 96.4047 | 97.431 | 97.5993 | 97.4719 | 97.2822 | 96.859 | 96.026 | 97.0747 | 97.3979 | 97.2268 | 96.9903 | 96.5138
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1190TL U B430 | PV Inverter | 624 | 682 | 800 | 430 | 1048.594 | CEC Inverter Database | 430V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1190TL-U-B430-430V | Y | 2550.2775 | 104.8594 | 209.7188 | 314.5782 | 524.297 | 786.4455 | 1048.594 | 96.0041 | 97.4811 | 97.8373 | 97.9231 | 97.7893 | 97.4138 | 95.8692 | 97.4303 | 97.7966 | 97.9039 | 97.781 | 97.4506 | 95.3825 | 97.1832 | 97.5935 | 97.7411 | 97.6496 | 97.3174
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1220TL U B440 | PV Inverter | 638 | 689 | 800 | 440 | 1099.306 | CEC Inverter Database | 440V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1220TL-U-B440-440V | Y | 2550.2775 | 109.9306 | 219.8612 | 329.7918 | 549.653 | 824.4795 | 1099.306 | 95.932 | 97.4927 | 97.868 | 97.9487 | 97.8105 | 97.4537 | 95.8363 | 97.4652 | 97.8509 | 97.9442 | 97.8039 | 97.4677 | 95.4261 | 97.2395 | 97.6478 | 97.8037 | 97.6832 | 97.3514
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1110TL U B400 | PV Inverter | 580 | 660 | 740 | 400 | 1110 | CEC Inverter Database | 400V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1110TL-U-B400-400V | Y | 80 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1250TL U B450 | PV Inverter | 652 | 696 | 800 | 450 | 1114.104 | CEC Inverter Database | 450V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1250TL-U-B450-450V | Y | 2550.2775 | 111.4104 | 222.8208 | 334.2312 | 557.052 | 835.578 | 1114.104 | 95.9706 | 97.5016 | 97.8688 | 97.9364 | 97.8103 | 97.4968 | 95.9001 | 97.4837 | 97.855 | 97.9743 | 97.8316 | 97.5204 | 95.5073 | 97.2604 | 97.6982 | 97.8443 | 97.7172 | 97.4132
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1275TL U B460 | PV Inverter | 666 | 703 | 800 | 460 | 1128.476 | CEC Inverter Database | 460V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1275TL-U-B460-460V | Y | 2550.2775 | 112.8476 | 225.6952 | 338.5428 | 564.238 | 846.357 | 1128.476 | 95.9938 | 97.508 | 97.8617 | 97.9706 | 97.8442 | 97.6278 | 95.8888 | 97.4823 | 97.8709 | 97.9916 | 97.8671 | 97.5597 | 95.5429 | 97.3202 | 97.7334 | 97.9123 | 97.7635 | 97.4905
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1165TL U B420 | PV Inverter | 610 | 675 | 740 | 420 | 1165 | CEC Inverter Database | 420V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1165TL-U-B420-420V | Y | 80 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1740TL U B670 | PV Inverter | 962 | 1081 | 1200 | 670 | 1272.412 | CEC Inverter Database | 670V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1740TL-U-B670-670V | Y | 459.0724 | 127.2412 | 254.4824 | 381.7236 | 636.206 | 954.309 | 1272.412 | 95.9646 | 97.3748 | 97.6902 | 97.7604 | 97.6287 | 97.348 | 95.7313 | 97.2879 | 97.5573 | 97.697 | 97.5442 | 97.223 | 95.3778 | 97.1365 | 97.419 | 97.506 | 97.402 | 97.144
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1800TL U B690 | PV Inverter | 962 | 1081 | 1200 | 690 | 1300.644 | CEC Inverter Database | 690V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1800TL-U-B690-690V | Y | 459.0724 | 130.0644 | 260.1288 | 390.1932 | 650.322 | 975.483 | 1300.644 | 96.6717 | 97.6652 | 97.8788 | 97.9021 | 97.7538 | 97.399 | 96.4722 | 97.5961 | 97.804 | 97.828 | 97.6778 | 97.3356 | 96.3335 | 97.5145 | 97.7082 | 97.7346 | 97.5625 | 97.2579
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1665TL U B640 | PV Inverter | 919 | 1060 | 1200 | 640 | 1367.076 | CEC Inverter Database | 640V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1665TL-U-B640-640V | Y | 459.0724 | 136.7076 | 273.4152 | 410.1228 | 683.538 | 1025.307 | 1367.076 | 96.2495 | 97.4423 | 97.7204 | 97.755 | 97.6184 | 97.3123 | 95.9772 | 97.3141 | 97.5906 | 97.6697 | 97.5061 | 97.1929 | 95.5155 | 97.1401 | 97.4064 | 97.4529 | 97.3426 | 97.0371
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1690TL U B650 | PV Inverter | 933 | 1067 | 1200 | 650 | 1375.282 | CEC Inverter Database | 650V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1690TL-U-B650-650V | Y | 459.0724 | 137.5282 | 275.0564 | 412.5846 | 687.641 | 1031.4615 | 1375.282 | 96.2881 | 97.5051 | 97.7757 | 97.8183 | 97.6619 | 97.3581 | 96.0008 | 97.4016 | 97.6638 | 97.7405 | 97.5736 | 97.2501 | 95.6676 | 97.2627 | 97.5419 | 97.5575 | 97.4238 | 97.0851
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1715TL U B660 | PV Inverter | 948 | 1074 | 1200 | 660 | 1390.614 | CEC Inverter Database | 660V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1715TL-U-B660-660V | Y | 459.0724 | 139.0614 | 278.1228 | 417.1842 | 695.307 | 1042.9605 | 1390.614 | 96.0622 | 97.4034 | 97.6863 | 97.7536 | 97.622 | 97.3392 | 95.8419 | 97.2707 | 97.5502 | 97.7009 | 97.5384 | 97.2305 | 95.3647 | 97.1092 | 97.4005 | 97.5253 | 97.4034 | 97.0865
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000H-ES | PV Inverter | 300 | 400 | 480 | 240 | 4.989 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000H-ES-240V | Y | 47.36 | 0.499 | 0.998 | 1.497 | 2.495 | 3.742 | 4.989 | 87.29 | 92.59 | 94.36 | 95.51 | 95.76 | 95.68 | 88.08 | 93.35 | 94.82 | 95.82 | 96.09 | 96.05 | 87.62 | 93.17 | 94.65 | 95.74 | 96.09 | 96.02
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000A-ES | PV Inverter | 300 | 400 | 480 | 240 | 5.0675 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000A-ES-240V | Y | 11.24 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000A-MS | PV Inverter | 300 | 400 | 480 | 240 | 5.0675 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000A-MS-240V | Y | 11.24 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000A-MS | PV Inverter | 300 | 400 | 480 | 208 | 5.133 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000A-MS-208V | Y | 9.31 | 0.5133 | 1.0266 | 1.5399 | 2.5665 | 3.8498 | 5.133 | 94.1098 | 96.0734 | 96.7353 | 97.0147 | 96.9328 | 96.7308 | 95.0838 | 96.7112 | 97.1772 | 97.3376 | 97.2176 | 97.0668 | 94.2209 | 96.3752 | 96.9856 | 97.2291 | 97.1353 | 96.9852
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW6000A-ES | PV Inverter | 360 | 400 | 480 | 240 | 6.109 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW6000A-ES-240V | Y | 9.3 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW6000A-MS | PV Inverter | 360 | 400 | 480 | 240 | 6.109 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW6000A-MS-240V | Y | 9.3 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW6000A-MS | PV Inverter | 360 | 400 | 480 | 240 | 6.138 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW6000A-MS-208V | Y | 11.5 | 0.6138 | 1.2276 | 1.8414 | 3.069 | 4.6035 | 6.138 | 95.1243 | 96.7475 | 97.0778 | 97.1859 | 96.9518 | 96.6585 | 95.4926 | 96.9805 | 97.2832 | 97.3147 | 97.0895 | 96.7862 | 95.1308 | 96.7711 | 97.1405 | 97.3004 | 97.0383 | 96.7392
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7000A-MS | PV Inverter | 210 | 400 | 480 | 208 | 7.007 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7000A-MS-208V | Y | 9.34 | 0.7007 | 1.4014 | 2.1021 | 3.5035 | 5.2553 | 7.007 | 94.2187 | 95.7079 | 96.1084 | 96.2315 | 95.9417 | 95.6578 | 95.7596 | 96.9959 | 97.2728 | 97.3125 | 97.1223 | 96.8193 | 95.1508 | 96.6691 | 97.0496 | 97.1497 | 96.9746 | 96.6823
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7000A-ES | PV Inverter | 210 | 400 | 480 | 240 | 7.057 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7000A-ES-240V | Y | 9.48 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7000A-MS | PV Inverter | 210 | 400 | 480 | 240 | 7.057 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7000A-MS-240V | Y | 9.48 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7600A-MS | PV Inverter | 230 | 400 | 480 | 208 | 7.61 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7600A-MS-208V | Y | 9.58 | 0.761 | 1.522 | 2.283 | 3.805 | 5.7075 | 7.61 | 94.5466 | 95.9281 | 96.2648 | 96.3508 | 96.0423 | 95.6545 | 95.9428 | 97.0933 | 97.3304 | 97.3007 | 97.0466 | 96.6994 | 95.3873 | 96.7795 | 97.0987 | 97.1136 | 96.8863 | 96.5432
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7600A-ES | PV Inverter | 230 | 400 | 480 | 240 | 7.644 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7600A-ES-240V | Y | 9.44 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7600A-MS | PV Inverter | 230 | 400 | 480 | 240 | 7.644 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7600A-MS-240V | Y | 9.44 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW8600A-MS | PV Inverter | 260 | 400 | 480 | 208 | 8.612 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW8600A-MS-208V | Y | 9.87 | 0.8612 | 1.7224 | 2.5836 | 4.306 | 6.459 | 8.612 | 95.1683 | 96.2326 | 96.481 | 96.4873 | 96.0901 | 95.6801 | 96.2574 | 97.1978 | 97.3196 | 97.1885 | 96.8348 | 96.3944 | 95.7378 | 96.9162 | 97.1345 | 97.1567 | 96.792 | 96.3471
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW8600A-ES | PV Inverter | 260 | 400 | 480 | 240 | 8.614 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW8600A-ES-240V | Y | 9.54 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW8600A-MS | PV Inverter | 260 | 400 | 480 | 240 | 8.614 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW8600A-MS-240V | Y | 9.54 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600H-ES | PV Inverter | 300 | 400 | 480 | 240 | 9.519 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600H-ES-240V | Y | 45.22 | 0.9519 | 1.9038 | 2.8557 | 4.7595 | 7.1393 | 9.519 | 92.2072 | 94.7398 | 95.3899 | 95.5471 | 95.1557 | 94.5552 | 93.0285 | 95.4529 | 96.0211 | 96.1062 | 95.7384 | 95.1732 | 92.6051 | 95.1829 | 95.7232 | 95.9558 | 95.6413 | 94.9918
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600A-ES | PV Inverter | 300 | 400 | 480 | 240 | 9.628 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600A-ES-240V | Y | 9.4 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600A-MS | PV Inverter | 300 | 400 | 480 | 208 | 9.628 | CEC Inverter Database | 208V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600A-MS-208V | Y | 9.67 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.688 | 96.5402 | 96.7441 | 96.5807 | 96.1525 | 95.6874 | 96.474 | 97.2271 | 97.2978 | 97.0928 | 96.6375 | 96.1254 | 95.999 | 96.9906 | 97.1322 | 96.9389 | 96.682 | 96.131
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600A-MS | PV Inverter | 300 | 400 | 480 | 240 | 9.628 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600A-MS-240V | Y | 9.4 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369
Jinko Solar Co., Ltd | JKMS260M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS260M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS265M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS265M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS270M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS270M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS275M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS275M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS275M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS275M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS280M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS280M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS280M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS280M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS285M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS285M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS285M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS285M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS290M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS290M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS290M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS290M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS295M-60B-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS295M-60B-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS295M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS295M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS300M-60-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.23 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS300M-60-EP-240V | Y | 0.03 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835
Jinko Solar Co., Ltd | JKMS300M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS300M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS300M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS300M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS300M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS300M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS300M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS300M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS305M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS305M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS305M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS305M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS305M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS305M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS305M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS305M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS305M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS305M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS305M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS305M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS305M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS305M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS305M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS305M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS310M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS310M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS310M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS310M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS310M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS310M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS310M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS310M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS310M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS310M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS310M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS310M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS310M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS310M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS310M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS310M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS315M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS315M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS315M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS315M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS315M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS315M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS315M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS315M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS315M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS315M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS315M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS315M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS315M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS315M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS315M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS315M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS320M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS320M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS320M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS320M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS320M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS320M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS320M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS320M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS320M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS320M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS320M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS320M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS320M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS320M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS320M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS320M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS325M-60BL-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS325M-60BL-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS325M-60BL-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS325M-60BL-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS325M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS325M-60BL-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS325M-60BL-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS325M-60BL-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS325M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS325M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS325M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS325M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS325M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS325M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS325M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS325M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS330M-60L-EP | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS330M-60L-EP-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS330M-60L-EP | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS330M-60L-EP-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
Jinko Solar Co., Ltd | JKMS330M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 208 | 0.24 | CEC Inverter Database | 208V | Jinko-Solar-Co.,-Ltd-JKMS330M-60L-EP-Q-208V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253
Jinko Solar Co., Ltd | JKMS330M-60L-EP-Q | PV Inverter | 27 | 32 | 37 | 240 | 0.24 | CEC Inverter Database | 240V | Jinko-Solar-Co.,-Ltd-JKMS330M-60L-EP-Q-240V | Y | 0.025 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107
KACO new energy GmbH | KACO blueplanet 110 TL3 M1 WM OD IIK0 | PV Inverter | 705 | 854 | 1300 | 480 | 109.765 | CEC Inverter Database | 480V | KACO-new-energy-GmbH-KACO-blueplanet-110-TL3-M1-WM-OD-IIK0-480V | Y | 5 | 10.9765 | 21.9531 | 32.9296 | 54.8827 | 82.324 | 109.7653 | 98.9285 | 99.0714 | 99.0635 | 98.972 | 98.8189 | 98.6338 | 98.5843 | 98.8565 | 98.883 | 98.797 | 98.6085 | 98.3579 | 97.5363 | 98.113 | 98.2893 | 98.3433 | 98.2373 | 98.0193
KACO new energy GmbH | KACO blueplanet 110 TL3 M1 WM OD IIKX | PV Inverter | 705 | 854 | 1300 | 480 | 109.765 | CEC Inverter Database | 480V | KACO-new-energy-GmbH-KACO-blueplanet-110-TL3-M1-WM-OD-IIKX-480V | Y | 5 | 10.9765 | 21.9531 | 32.9296 | 54.8827 | 82.324 | 109.7653 | 98.9285 | 99.0714 | 99.0635 | 98.972 | 98.8189 | 98.6338 | 98.5843 | 98.8565 | 98.883 | 98.797 | 98.6085 | 98.3579 | 97.5363 | 98.113 | 98.2893 | 98.3433 | 98.2373 | 98.0193
KACO new energy GmbH | KACO blueplanet 125 TL3 M1 WM OD IIP0 | PV Inverter | 875 | 981 | 1300 | 600 | 138.663 | CEC Inverter Database | 600V | KACO-new-energy-GmbH-KACO-blueplanet-125-TL3-M1-WM-OD-IIP0-600V | Y | 5.57 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931
KACO new energy GmbH | KACO blueplanet 125 TL3 M1 WM OD IIPX | PV Inverter | 875 | 981 | 1300 | 600 | 138.663 | CEC Inverter Database | 600V | KACO-new-energy-GmbH-KACO-blueplanet-125-TL3-M1-WM-OD-IIPX-600V | Y | 5.57 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931
KACO new energy GmbH | KACO blueplanet 137 TL3 M1 WM OD IIP0 | PV Inverter | 875 | 981 | 1300 | 600 | 138.663 | CEC Inverter Database | 600V | KACO-new-energy-GmbH-KACO-blueplanet-137-TL3-M1-WM-OD-IIP0-600V | Y | 5.57 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931
KACO new energy GmbH | KACO blueplanet 137 TL3 M1 WM OD IIPX | PV Inverter | 875 | 981 | 1300 | 600 | 138.663 | CEC Inverter Database | 600V | KACO-new-energy-GmbH-KACO-blueplanet-137-TL3-M1-WM-OD-IIPX-600V | Y | 5.57 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931
KACO new energy GmbH | KACO blueplanet 150 TL3 M1 WM OD IIQ0 | PV Inverter | 960 | 1045 | 1300 | 660 | 151.228 | CEC Inverter Database | 660V | KACO-new-energy-GmbH-KACO-blueplanet-150-TL3-M1-WM-OD-IIQ0-660V | Y | 5.25 | 15.1228 | 30.2455 | 45.3683 | 75.6138 | 113.4207 | 151.2276 | 98.8336 | 99.11 | 99.1489 | 99.1038 | 99.0103 | 98.8953 | 98.6981 | 99.001 | 99.0493 | 99.0136 | 98.8922 | 98.7227 | 98.1102 | 98.5923 | 98.7418 | 98.7863 | 98.698 | 98.5522
KACO new energy GmbH | KACO blueplanet 150 TL3 M1 WM OD IIQX | PV Inverter | 960 | 1045 | 1300 | 660 | 151.228 | CEC Inverter Database | 660V | KACO-new-energy-GmbH-KACO-blueplanet-150-TL3-M1-WM-OD-IIQX-660V | Y | 5.25 | 15.1228 | 30.2455 | 45.3683 | 75.6138 | 113.4207 | 151.2276 | 98.8336 | 99.11 | 99.1489 | 99.1038 | 99.0103 | 98.8953 | 98.6981 | 99.001 | 99.0493 | 99.0136 | 98.8922 | 98.7227 | 98.1102 | 98.5923 | 98.7418 | 98.7863 | 98.698 | 98.5522
LeadSolar Energy Co., Ltd | LS600 | PV Inverter | 27 | 36 | 45 | 240 | 0.5 | CEC Inverter Database | 240V | LeadSolar-Energy-Co.,-Ltd-LS600-240V | Y | 0.09 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5
LeadSolar Energy Co., Ltd | LS700S | PV Inverter | 52 | 54 | 56 | 208 | 0.606 | CEC Inverter Database | 208V | LeadSolar-Energy-Co.,-Ltd-LS700S-208V | Y | 0.21 | 0.06058 | 0.12116 | 0.18174 | 0.3029 | 0.45435 | 0.60579 | 91.2178 | 94.3165 | 94.9482 | 95.4648 | 95.5662 | 95.3209 | 90.0557 | 93.6949 | 94.9532 | 95.7014 | 95.816 | 95.5133 | 90.1569 | 93.9414 | 95.0073 | 95.3558 | 95.8147 | 95.555
LeadSolar Energy Co., Ltd | LS600X | PV Inverter | 50 | 57 | 64 | 240 | 0.708 | CEC Inverter Database | 240V | LeadSolar-Energy-Co.,-Ltd-LS600X-240V | Y | 0.16 | 0.0708 | 0.1416 | 0.2124 | 0.354 | 0.531 | 0.708 | 89.3868 | 93.5464 | 95.134 | 96.2627 | 96.5776 | 96.3824 | 90.1881 | 93.8539 | 95.2694 | 96.306 | 96.5948 | 96.5453 | 87.474 | 92.8944 | 95.0621 | 96.0676 | 96.4861 | 96.4858
LG Electronics Inc. | LG315E1K-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG315E1K-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG315E1K-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG315E1K-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG320E1K-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG320E1K-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG320E1K-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG320E1K-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG325E1C-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG325E1C-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG325E1C-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG325E1C-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG325E1K-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG325E1K-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG325E1K-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG325E1K-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG330E1C-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG330E1C-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG330E1C-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG330E1C-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG335E1C-A5 | PV Inverter | 27 | 36 | 45 | 208 | 0.28 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG335E1C-A5-208V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6 | 96.3 | 96.9 | 97.4 | 97.1 | 96.6 | 94.6 | 95.7 | 96.5 | 97.1 | 97.1 | 96.7 | 93.9 | 95 | 96 | 96.9 | 96.9 | 96.6 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG335E1C-A5 | PV Inverter | 27 | 36 | 45 | 240 | 0.28 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG335E1C-A5-240V | Y | 0.02 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
LG Electronics Inc. | LG355A1C-A5 | PV Inverter | 32 | 35 | 42 | 208 | 0.32 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG355A1C-A5-208V | Y | 0.85 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8
LG Electronics Inc. | LG355A1C-A5 | PV Inverter | 32 | 35 | 42 | 240 | 0.32 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG355A1C-A5-240V | Y | 0.16 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8
LG Electronics Inc. | LG360A1C-A5 | PV Inverter | 32 | 35 | 42 | 208 | 0.32 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG360A1C-A5-208V | Y | 0.85 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8
LG Electronics Inc. | LG360A1C-A5 | PV Inverter | 32 | 35 | 42 | 240 | 0.32 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG360A1C-A5-240V | Y | 0.16 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8
LG Electronics Inc. | LG365A1C-A5 | PV Inverter | 32 | 35 | 42 | 208 | 0.32 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG365A1C-A5-208V | Y | 0.85 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8
LG Electronics Inc. | LG365A1C-A5 | PV Inverter | 32 | 35 | 42 | 240 | 0.32 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG365A1C-A5-240V | Y | 0.16 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8
LG Electronics Inc. | LG370A1C-A5 | PV Inverter | 32 | 35 | 42 | 208 | 0.32 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG370A1C-A5-208V | Y | 0.85 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8
LG Electronics Inc. | LG370A1C-A5 | PV Inverter | 32 | 35 | 42 | 240 | 0.32 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG370A1C-A5-240V | Y | 0.16 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8
LG Electronics Inc. | LG340M1K-L5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG340M1K-L5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG345M1K-L5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG345M1K-L5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG350M1K-L5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG350M1K-L5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG355M1C-N5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG355M1C-N5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG355M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG355M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG360A1K-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG360A1K-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG360M1C-N5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG360M1C-N5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG360M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG360M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG365A1C-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG365A1C-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG365A1K-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG365A1K-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG365M1C-N5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG365M1C-N5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG365M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG365M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG370A1C-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG370A1C-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG370M1C-N5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG370M1C-N5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG370M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG370M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG375A1C-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG375A1C-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG375M1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG375M1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG375M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG375M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG380A1C-V5 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG380A1C-V5-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG380M1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG380M1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG380M1K-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG380M1K-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG385M1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG385M1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG395A1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG395A1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG400A1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG400A1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG405A1C-A6 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LG405A1C-A6-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LM320UE-A2 | PV Inverter | 32 | 35 | 42 | 240 | 0.321 | CEC Inverter Database | 240V | LG-Electronics-Inc.-LM320UE-A2-240V | Y | 0.15 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997
LG Electronics Inc. | LG340M1K-L5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG340M1K-L5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG345M1K-L5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG345M1K-L5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG350M1K-L5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG350M1K-L5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG355M1C-N5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG355M1C-N5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG355M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG355M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG360A1K-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG360A1K-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG360M1C-N5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG360M1C-N5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG360M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG360M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG365A1C-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG365A1C-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG365A1K-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG365A1K-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG365M1C-N5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG365M1C-N5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG365M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG365M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG370A1C-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG370A1C-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG370M1C-N5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG370M1C-N5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG370M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG370M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG375A1C-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG375A1C-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG375M1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG375M1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG375M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG375M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG380A1C-V5 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG380A1C-V5-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG380M1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG380M1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG380M1K-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG380M1K-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG385M1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG385M1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG395A1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG395A1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG400A1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG400A1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LG405A1C-A6 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LG405A1C-A6-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | LM320UE-A2 | PV Inverter | 32 | 35 | 42 | 208 | 0.322 | CEC Inverter Database | 208V | LG-Electronics-Inc.-LM320UE-A2-208V | Y | 0.11 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934
LG Electronics Inc. | D007KEEN261 | PV Inverter | 270 | 380 | 450 | 208 | 6.656 | CEC Inverter Database | 208V | LG-Electronics-Inc.-D007KEEN261-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 95.0392 | 96.9541 | 97.466 | 97.7308 | 97.5103 | 97.1462
LG Electronics Inc. | D007KEEN261 | PV Inverter | 270 | 380 | 450 | 240 | 7.68 | CEC Inverter Database | 240V | LG-Electronics-Inc.-D007KEEN261-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 95.7683 | 97.3217 | 97.8155 | 97.9581 | 97.748 | 97.4471
NeoVolta Inc. | NV7600 | PV Inverter | 240 | 370 | 425 | 208 | 7.4473 | CEC Inverter Database | 208V | NeoVolta-Inc.-NV7600-208V | Y | 13.4 | 0.74473 | 1.4895 | 2.2342 | 3.7237 | 5.5855 | 7.4473 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631
NeoVolta Inc. | NV7600 | PV Inverter | 240 | 370 | 425 | 240 | 7.657 | CEC Inverter Database | 240V | NeoVolta-Inc.-NV7600-240V | Y | 13.4 | 0.76571 | 1.5314 | 2.2971 | 3.8286 | 5.7428 | 7.6571 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868
Northern Electric & Power Co. Ltd | BDM-800-208A | PV Inverter | 22 | 35 | 55 | 208 | 0.707 | CEC Inverter Database | 208V | Northern-Electric-&-Power-Co.-Ltd-BDM-800-208A-208V | Y | 0.1 | 0.0707 | 0.1414 | 0.2121 | 0.3535 | 0.53025 | 0.707 | 93.6599 | 95.599 | 96.961 | 96.8296 | 96.6237 | 96.4904 | 92.606 | 96.1692 | 96.8496 | 96.8689 | 96.6824 | 96.1217 | 93.4666 | 94.8875 | 97.0612 | 96.8756 | 96.6955 | 96.4379
Northern Electric & Power Co. Ltd | BDM-800-240A | PV Inverter | 22 | 35 | 55 | 240 | 0.772 | CEC Inverter Database | 240V | Northern-Electric-&-Power-Co.-Ltd-BDM-800-240A-240V | Y | 0.1 | 0.0772 | 0.1544 | 0.2316 | 0.386 | 0.579 | 0.772 | 94.2089 | 95.8335 | 96.8654 | 97.0732 | 96.5892 | 96.0902 | 93.9535 | 96.8628 | 96.6484 | 97.0781 | 96.979 | 96.4291 | 93.4666 | 95.9837 | 96.7742 | 96.7578 | 96.6548 | 96.416
ONE SUN, MEXICO S.A. DE C.V. | 1S480-10k | PV Inverter | 450 | 750 | 850 | 480 | 9.975 | CEC Inverter Database | 480V | ONE-SUN,-MEXICO-S.A.-DE-C.V.-1S480-10k-480V | Y | 8.3 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2
OutBack Power Technologies, Inc. | SBX5048-120/240 | PV Inverter | 250 | 420 | 550 | 240 | 4.985 | CEC Inverter Database | 240V | OutBack-Power-Technologies,-Inc.-SBX5048-120-240-240V | Y | 24.85 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173
OutBack Power Technologies, Inc. | PHXL480-10k | PV Inverter | 450 | 750 | 850 | 480 | 9.975 | CEC Inverter Database | 480V | OutBack-Power-Technologies,-Inc.-PHXL480-10k-480V | Y | 8.3 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2
Pika Energy | X7603 | PV Inverter | 390 | 400 | 420 | 240 | 7.585 | CEC Inverter Database | 240V | Pika-Energy-X7603-240V | Y | 1.29 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9
Pika Energy | X7601 | PV Inverter | 390 | 400 | 420 | 240 | 7.587 | CEC Inverter Database | 240V | Pika-Energy-X7601-240V | Y | 1.29 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9
Pika Energy | X7602 | PV Inverter | 390 | 400 | 420 | 240 | 7.587 | CEC Inverter Database | 240V | Pika-Energy-X7602-240V | Y | 1.29 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91
Pika Energy | X11403 | PV Inverter | 390 | 400 | 420 | 208 | 11.18 | CEC Inverter Database | 208V | Pika-Energy-X11403-208V | Y | 0.13 | 1.12 | 2.24 | 3.35 | 5.59 | 8.39 | 11.18 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9
Pika Energy | X11402 | PV Inverter | 390 | 400 | 420 | 208 | 11.187 | CEC Inverter Database | 208V | Pika-Energy-X11402-208V | Y | 0.13 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9
POMCube Inc. | PNZ-10K1N2-NA0 | PV Inverter | 250 | 360 | 530 | 240 | 9.923 | CEC Inverter Database | 240V | POMCube-Inc.-PNZ-10K1N2-NA0-240V | Y | 21.92 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581
Power Electronics | FS1050CU15 | PV Inverter | 800 | 900 | 1200 | 565 | 1163.5 | CEC Inverter Database | 565V | Power-Electronics-FS1050CU15-565V | Y | 338.51 | 116 | 233 | 349 | 582 | 873 | 1164 | 93 | 96.2 | 96.7 | 97.5 | 97.6 | 97.5 | 93 | 96.1 | 96.7 | 97.4 | 97.5 | 97.3 | 93.2 | 96.2 | 96.6 | 97.4 | 97.6 | 97.3
Power Electronics | FS1100CU15O3 | PV Inverter | 849 | 940 | 1200 | 600 | 1176.44 | CEC Inverter Database | 600V | Power-Electronics-FS1100CU15O3-600V | Y | 358.91 | 118 | 235 | 353 | 588 | 882 | 1176 | 95.9 | 97.5 | 97.7 | 98 | 98 | 98 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9
Power Electronics | FS1100CU15 | PV Inverter | 849 | 940 | 1200 | 600 | 1209.25 | CEC Inverter Database | 600V | Power-Electronics-FS1100CU15-600V | Y | 347.22 | 121 | 242 | 363 | 605 | 907 | 1209 | 93.1 | 96.2 | 96.8 | 97.5 | 97.8 | 97.7 | 93.1 | 96.1 | 96.8 | 97.5 | 97.6 | 97.6 | 93.2 | 96.2 | 96.7 | 97.5 | 97.7 | 97.5
Power Electronics | FS1200CU15 | PV Inverter | 913 | 980 | 1200 | 645 | 1300.9 | CEC Inverter Database | 645V | Power-Electronics-FS1200CU15-645V | Y | 348.45 | 130 | 260 | 390 | 650 | 976 | 1301 | 93.5 | 96.5 | 97 | 97.7 | 97.8 | 97.7 | 93.5 | 96.5 | 96.9 | 97.6 | 97.7 | 97.6 | 93.5 | 96.5 | 96.9 | 97.6 | 97.8 | 97.6
Power Electronics | FS1275CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 1389.08 | CEC Inverter Database | 690V | Power-Electronics-FS1275CU15-690V | Y | 353.05 | 139 | 278 | 417 | 695 | 1042 | 1389 | 91.8 | 95.5 | 96.2 | 97.7 | 97.9 | 97.8 | 91.7 | 95.5 | 96.3 | 97.6 | 97.8 | 97.6 | 91.9 | 95.6 | 96.3 | 97.6 | 97.8 | 97.6
Power Electronics | FS1400CU15 | PV Inverter | 800 | 900 | 1200 | 565 | 1517.09 | CEC Inverter Database | 565V | Power-Electronics-FS1400CU15-565V | Y | 359.56 | 152 | 303 | 455 | 759 | 1138 | 1517 | 94.3 | 96.5 | 97.3 | 97.7 | 97.8 | 97.6 | 94.3 | 96.4 | 97.2 | 97.7 | 97.7 | 97.5 | 94.4 | 96.5 | 97.2 | 97.6 | 97.7 | 97.5
Power Electronics | FS1500CU15O3 | PV Inverter | 849 | 940 | 1200 | 600 | 1594.72 | CEC Inverter Database | 600V | Power-Electronics-FS1500CU15O3-600V | Y | 379.71 | 159 | 319 | 478 | 797 | 1196 | 1595 | 96.9 | 97.6 | 97.9 | 98.1 | 98 | 97.9 | 96.6 | 97.5 | 97.8 | 98 | 98 | 97.8 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8
Power Electronics | FS1475CU15 | PV Inverter | 849 | 940 | 1200 | 600 | 1610.37 | CEC Inverter Database | 600V | Power-Electronics-FS1475CU15-600V | Y | 368.71 | 161 | 322 | 483 | 805 | 1208 | 1610 | 94.5 | 96.7 | 97.5 | 97.8 | 97.9 | 97.6 | 94.5 | 96.6 | 97.4 | 97.8 | 97.8 | 97.6 | 94.6 | 96.6 | 97.4 | 97.7 | 97.8 | 97.5
Power Electronics | FS1600CU15 | PV Inverter | 913 | 980 | 1200 | 645 | 1734.81 | CEC Inverter Database | 645V | Power-Electronics-FS1600CU15-645V | Y | 373.96 | 173 | 347 | 520 | 867 | 1301 | 1735 | 94.7 | 96.8 | 97.5 | 98 | 98 | 97.8 | 94.7 | 96.8 | 97.5 | 97.9 | 97.9 | 97.7 | 94.7 | 96.8 | 97.5 | 97.8 | 97.9 | 97.7
Power Electronics | FS1700CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 1850.63 | CEC Inverter Database | 690V | Power-Electronics-FS1700CU15-690V | Y | 368.51 | 185 | 370 | 555 | 925 | 1388 | 1851 | 95 | 97 | 97.7 | 98.1 | 98.2 | 97.9 | 94.9 | 97 | 97.6 | 98.1 | 98 | 97.9 | 94.9 | 96.9 | 97.6 | 98 | 98.1 | 97.8
Power Electronics | FS1750CU15 | PV Inverter | 800 | 900 | 1200 | 565 | 1896.53 | CEC Inverter Database | 565V | Power-Electronics-FS1750CU15-565V | Y | 378.47 | 190 | 379 | 569 | 948 | 1422 | 1897 | 94.8 | 96.6 | 97.4 | 98 | 97.9 | 97.7 | 94.8 | 96.5 | 97.3 | 97.8 | 97.8 | 97.6 | 94.7 | 96.4 | 97.3 | 97.8 | 97.8 | 97.5
Power Electronics | FS1850CU15O3 | PV Inverter | 849 | 940 | 1200 | 600 | 1974.29 | CEC Inverter Database | 600V | Power-Electronics-FS1850CU15O3-600V | Y | 397.3 | 197 | 395 | 592 | 987 | 1481 | 1974 | 96.9 | 97.7 | 97.9 | 98.1 | 98.1 | 97.9 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 96.8 | 97.6 | 97.9 | 98 | 98 | 97.8
Power Electronics | FS1850CU15 | PV Inverter | 849 | 940 | 1200 | 600 | 2020.96 | CEC Inverter Database | 600V | Power-Electronics-FS1850CU15-600V | Y | 388.77 | 202 | 404 | 606 | 1010 | 1516 | 2021 | 95.1 | 96.7 | 97.5 | 98 | 98 | 97.8 | 95 | 96.6 | 97.5 | 97.9 | 97.9 | 97.7 | 95 | 96.6 | 97.4 | 97.9 | 97.9 | 97.6
Power Electronics | FS2000K | PV Inverter | 849 | 940 | 1200 | 600 | 2103.416 | CEC Inverter Database | 600V | Power-Electronics-FS2000K-600V | Y | 442.59 | 210.3416 | 420.6832 | 631.0248 | 1051.708 | 1577.562 | 2103.416 | 96.0919 | 97.5238 | 97.9704 | 98.3806 | 98.2078 | 97.9134 | 96.1235 | 97.504 | 97.9438 | 98.2085 | 98.1306 | 97.7279 | 96.1964 | 97.4535 | 97.9859 | 98.3557 | 98.141 | 97.7477
Power Electronics | FS2000CU15 | PV Inverter | 913 | 980 | 1200 | 645 | 2162.42 | CEC Inverter Database | 645V | Power-Electronics-FS2000CU15-645V | Y | 388.97 | 216 | 432 | 649 | 1081 | 1622 | 2162 | 95.2 | 96.9 | 97.6 | 98.1 | 98.1 | 97.9 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8
Power Electronics | FS2000M | PV Inverter | 849 | 940 | 1200 | 34500 | 2178.068 | CEC Inverter Database | 34000V | Power-Electronics-FS2000M-34000V | Y | 5970 | 217.8068 | 435.6136 | 653.4204 | 1089.034 | 1633.551 | 2178.068 | 93.4983 | 95.9935 | 96.8011 | 97.4581 | 97.6572 | 97.5548 | 93.3492 | 95.8983 | 96.8261 | 97.396 | 97.5629 | 97.4223 | 93.4114 | 95.9287 | 96.709 | 97.3923 | 97.6181 | 97.4835
Power Electronics | FS2125K | PV Inverter | 849 | 940 | 1200 | 600 | 2201.52 | CEC Inverter Database | 600V | Power-Electronics-FS2125K-600V | Y | 302.3 | 220.152 | 440.304 | 660.456 | 1100.76 | 1651.14 | 2201.52 | 95.8049 | 97.3563 | 97.9723 | 98.3071 | 98.258 | 98.0579 | 95.7119 | 97.2529 | 97.8692 | 98.2153 | 98.1268 | 97.9016 | 95.6723 | 97.2384 | 97.8428 | 98.218 | 98.1248 | 97.8825
Power Electronics | FS2180K | PV Inverter | 870 | 950 | 1200 | 615 | 2259.5 | CEC Inverter Database | 615V | Power-Electronics-FS2180K-615V | Y | 302.3 | 225.95 | 451.9 | 677.85 | 1129.75 | 1694.625 | 2259.5 | 95.8228 | 97.3376 | 97.9902 | 98.3143 | 98.2785 | 98.0989 | 95.7355 | 97.2693 | 97.8894 | 98.26 | 98.2178 | 97.9983 | 95.7021 | 97.2507 | 97.8775 | 98.2343 | 98.2056 | 97.9913
Power Electronics | FS2100CU15 | PV Inverter | 800 | 900 | 1200 | 565 | 2275.89 | CEC Inverter Database | 565V | Power-Electronics-FS2100CU15-565V | Y | 398.85 | 228 | 455 | 683 | 1138 | 1707 | 2276 | 95.4 | 97.2 | 97.6 | 98 | 98 | 97.7 | 95.2 | 97.1 | 97.6 | 97.9 | 97.8 | 97.6 | 95.3 | 97 | 97.5 | 97.9 | 97.8 | 97.6
Power Electronics | FS2125CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 2306.41 | CEC Inverter Database | 690V | Power-Electronics-FS2125CU15-690V | Y | 390.63 | 231 | 461 | 692 | 1153 | 1730 | 2306 | 95.6 | 97.1 | 97.8 | 98.2 | 98.2 | 98 | 95.6 | 97.1 | 97.7 | 98.1 | 98.1 | 97.9 | 95.5 | 97 | 97.6 | 98.1 | 98.1 | 97.8
Power Electronics | FS2225CU15 | PV Inverter | 849 | 940 | 1200 | 600 | 2417.08 | CEC Inverter Database | 600V | Power-Electronics-FS2225CU15-600V | Y | 403.32 | 242 | 483 | 725 | 1209 | 1813 | 2417 | 95.5 | 97.2 | 97.7 | 98.1 | 98.1 | 97.8 | 95.5 | 97.2 | 97.7 | 98 | 98 | 97.7 | 95.4 | 97.1 | 97.6 | 98 | 98 | 97.7
Power Electronics | FS2250CU15O3 | PV Inverter | 849 | 940 | 1200 | 600 | 2420.37 | CEC Inverter Database | 600V | Power-Electronics-FS2250CU15O3-600V | Y | 416.47 | 242 | 484 | 726 | 1210 | 1815 | 2420 | 97.2 | 97.8 | 98 | 98.2 | 98.1 | 97.9 | 96.9 | 97.8 | 98 | 98 | 98 | 97.7 | 96.9 | 97.7 | 97.9 | 98.1 | 98 | 97.8
Power Electronics | FS2150CU15 | PV Inverter | 913 | 980 | 1200 | 645 | 2558.48 | CEC Inverter Database | 645V | Power-Electronics-FS2150CU15-645V | Y | 409.99 | 256 | 512 | 768 | 1279 | 1919 | 2558 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 95.6 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 95.6 | 97.3 | 97.7 | 98.1 | 98.1 | 97.8
Power Electronics | FS2400CU15 | PV Inverter | 913 | 980 | 1200 | 645 | 2583.76 | CEC Inverter Database | 645V | Power-Electronics-FS2400CU15-645V | Y | 407.44 | 258 | 517 | 775 | 1292 | 1938 | 2584 | 95.8 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 95.8 | 97.4 | 97.7 | 98.1 | 98.1 | 97.8 | 95.7 | 97.3 | 97.7 | 98.1 | 98 | 97.8
Power Electronics | FS2450CU15 | PV Inverter | 800 | 900 | 1200 | 565 | 2664.07 | CEC Inverter Database | 565V | Power-Electronics-FS2450CU15-565V | Y | 417.35 | 266 | 533 | 799 | 1332 | 1998 | 2664 | 95.7 | 97.3 | 97.6 | 98 | 98 | 97.7 | 95.6 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 95.6 | 97.2 | 97.5 | 97.9 | 97.9 | 97.6
Power Electronics | FS2550CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 2759.39 | CEC Inverter Database | 690V | Power-Electronics-FS2550CU15-690V | Y | 408.29 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 96 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 95.9 | 97.4 | 97.8 | 98.2 | 98.1 | 97.8 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9
Power Electronics | FS2300CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 2759.49 | CEC Inverter Database | 690V | Power-Electronics-FS2300CU15-690V | Y | 408.67 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 98 | 95.8 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 95.8 | 97.4 | 97.8 | 98.2 | 98.1 | 97.9
Power Electronics | FS2600CU15O3 | PV Inverter | 849 | 940 | 1200 | 600 | 2770.2 | CEC Inverter Database | 600V | Power-Electronics-FS2600CU15O3-600V | Y | 433.54 | 277 | 554 | 831 | 1385 | 2078 | 2770 | 97.2 | 97.9 | 98.1 | 98.2 | 98.1 | 97.9 | 97.1 | 97.8 | 98 | 98 | 98 | 97.8 | 97.1 | 97.8 | 98 | 98.1 | 98 | 97.8
Power Electronics | FS2600CU15 | PV Inverter | 849 | 940 | 1200 | 600 | 2821.84 | CEC Inverter Database | 600V | Power-Electronics-FS2600CU15-600V | Y | 423.67 | 282 | 564 | 847 | 1411 | 2116 | 2822 | 95.7 | 97.4 | 97.9 | 98.1 | 98 | 97.8 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 97.7 | 95.7 | 97.2 | 97.7 | 98 | 98 | 97.7
Power Electronics | FS2840M | PV Inverter | 849 | 940 | 1200 | 34500 | 2844.7 | CEC Inverter Database | 34000V | Power-Electronics-FS2840M-34000V | Y | 5970 | 284.47 | 568.94 | 853.41 | 1422.35 | 2133.525 | 2844.7 | 94.4413 | 96.5602 | 97.2233 | 97.6279 | 97.7507 | 97.6516 | 94.3535 | 96.4533 | 97.1235 | 97.5301 | 97.6348 | 97.5292 | 94.3096 | 96.5127 | 97.1355 | 97.5968 | 97.707 | 97.5485
Power Electronics | FS3001M | PV Inverter | 849 | 940 | 1200 | 34500 | 3017.848 | CEC Inverter Database | 34000V | Power-Electronics-FS3001M-34000V | Y | 6084 | 301.7848 | 603.5696 | 905.3544 | 1508.924 | 2263.386 | 3017.848 | 94.6253 | 96.6462 | 97.2747 | 97.6765 | 97.7113 | 97.5625 | 94.5552 | 96.5905 | 97.182 | 97.5764 | 97.6672 | 97.4448 | 94.5184 | 96.5838 | 97.1884 | 97.6148 | 97.7037 | 97.4863
Power Electronics | FS2800CU15 | PV Inverter | 913 | 940 | 1200 | 645 | 3024.91 | CEC Inverter Database | 645V | Power-Electronics-FS2800CU15-645V | Y | 427.54 | 302 | 605 | 907 | 1512 | 2269 | 3025 | 96 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.8 | 95.9 | 97.3 | 97.7 | 98.1 | 98 | 97.8
Power Electronics | FS3000M | PV Inverter | 849 | 940 | 1200 | 34500 | 3109.266 | CEC Inverter Database | 34000V | Power-Electronics-FS3000M-34000V | Y | 6056 | 310.9266 | 621.8532 | 932.7798 | 1554.633 | 2331.9495 | 3109.266 | 94.9749 | 96.8471 | 97.3723 | 97.6775 | 97.6602 | 97.3399 | 94.9428 | 96.7736 | 97.3237 | 97.6181 | 97.528 | 97.2027 | 94.9123 | 96.8194 | 97.3539 | 97.6385 | 97.5917 | 97.2755
Power Electronics | FS3000K | PV Inverter | 849 | 940 | 1200 | 600 | 3121.31 | CEC Inverter Database | 600V | Power-Electronics-FS3000K-600V | Y | 324.8 | 312.131 | 624.262 | 936.393 | 1560.655 | 2340.983 | 3121.31 | 96.5626 | 97.8243 | 98.1437 | 98.3712 | 98.2469 | 97.9269 | 96.4544 | 97.7066 | 98.0639 | 98.269 | 98.1285 | 97.8352 | 96.4381 | 97.7135 | 98.047 | 98.2775 | 98.1268 | 97.8519
Power Electronics | FS3000CU15 | PV Inverter | 976 | 1030 | 1200 | 690 | 3201.17 | CEC Inverter Database | 690V | Power-Electronics-FS3000CU15-690V | Y | 426.4 | 320 | 640 | 960 | 1601 | 2401 | 3201 | 96.1 | 97.5 | 97.9 | 98.2 | 98.3 | 98.1 | 96 | 97.5 | 97.9 | 98.1 | 98.2 | 98 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9
Power Electronics | FS3150K | PV Inverter | 891 | 970 | 1200 | 630 | 3279.87 | CEC Inverter Database | 630V | Power-Electronics-FS3150K-630V | Y | 324.8 | 327.987 | 655.974 | 983.961 | 1639.935 | 2459.903 | 3279.87 | 96.7726 | 97.5708 | 97.8887 | 98.1284 | 97.8074 | 97.6727 | 96.6921 | 97.4868 | 97.8106 | 98.0403 | 97.7237 | 97.5984 | 96.643 | 97.4589 | 97.7961 | 98.0568 | 97.874 | 97.5903
Power Electronics | FS3190K | PV Inverter | 849 | 940 | 1200 | 630 | 3303.82 | CEC Inverter Database | 600V | Power-Electronics-FS3190K-600V | Y | 324.8 | 330.382 | 660.764 | 991.146 | 1651.91 | 2477.865 | 3303.82 | 96.4208 | 97.7616 | 98.1336 | 98.3863 | 98.2416 | 97.9793 | 96.3008 | 97.6527 | 98.0358 | 98.2753 | 98.16 | 97.8879 | 96.335 | 97.6759 | 98.0457 | 98.2887 | 98.1634 | 97.9124
Power Electronics | FS3150M | PV Inverter | 891 | 970 | 1200 | 34500 | 3307.98 | CEC Inverter Database | 34000V | Power-Electronics-FS3150M-34000V | Y | 6880 | 330.798 | 661.596 | 992.394 | 1653.99 | 2480.985 | 3307.98 | 95.0211 | 96.9027 | 97.4342 | 97.7515 | 97.6422 | 97.3662 | 94.9579 | 96.7802 | 97.3562 | 97.6708 | 97.5884 | 97.2348 | 94.9742 | 96.7828 | 97.3475 | 97.6939 | 97.6 | 97.309
Power Electronics | FS3225M | PV Inverter | 913 | 980 | 1200 | 34500 | 3367.326 | CEC Inverter Database | 34000V | Power-Electronics-FS3225M-34000V | Y | 7640 | 336.7326 | 673.4652 | 1010.1978 | 1683.663 | 2525.4945 | 3367.326 | 95.0183 | 96.8928 | 97.3979 | 97.7634 | 97.7231 | 96.9255 | 94.9704 | 96.8221 | 97.331 | 97.6393 | 97.6318 | 96.8405 | 94.9604 | 96.7692 | 97.3276 | 97.6807 | 97.6328 | 97.003
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ-G1.3 | PV Inverter | 540 | 750 | 830 | 480 | 29.444 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-30-WZZZZZZ-G1.3-480V | Y | 35.14 | 2.9444 | 5.8889 | 8.8333 | 14.7222 | 22.0832 | 29.4443 | 86.7633 | 92.621 | 93.1032 | 93.8163 | 93.2421 | 92.0854 | 87.6485 | 93.2657 | 93.53 | 94.1163 | 93.4041 | 92.9205 | 88.6063 | 92.4924 | 94.6691 | 94.5469 | 93.6549 | 93.0472
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZ-G1.3 | PV Inverter | 540 | 750 | 830 | 480 | 29.956 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-30-ZZZZZZ-G1.3-480V | Y | 46.3 | 2.9956 | 5.9911 | 8.9867 | 14.9778 | 22.4667 | 29.9557 | 92.6541 | 95.1194 | 96.0767 | 96.8464 | 96.977 | 96.8538 | 93.7759 | 95.2415 | 96.5013 | 97.1768 | 97.3758 | 97.3985 | 92.7942 | 94.8855 | 96.3887 | 97.0579 | 97.1908 | 97.4251
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-G1.5 | PV Inverter | 350 | 710 | 830 | 480 | 124.964 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-125XXXXXX-G1.5-480V | Y | 68 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 87.1196 | 92.9413 | 94.9723 | 95.2179 | 95.6593 | 95.2115 | 91.9189 | 95.3761 | 95.8979 | 96.6258 | 96.8865 | 96.649 | 91.5596 | 95.713 | 96.4245 | 96.9684 | 96.936 | 96.8929
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-W-G1.5 | PV Inverter | 350 | 710 | 830 | 480 | 124.964 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-125XXXXXX-W-G1.5-480V | Y | 68 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 84.9387 | 91.6494 | 93.8422 | 94.0171 | 94.1574 | 93.2247 | 89.6179 | 94.0504 | 94.7567 | 95.4072 | 95.3654 | 94.6322 | 89.2675 | 94.3826 | 95.2771 | 95.7455 | 95.4141 | 94.8711
Rhombus Energy Solutions | RES-BESS60DP-480 | PV Inverter | 270 | 441 | 870 | 480 | 59.789 | CEC Inverter Database | 480V | Rhombus-Energy-Solutions-RES-BESS60DP-480-480V | Y | 92 | 5.9789 | 11.9578 | 17.9367 | 29.8945 | 44.8418 | 59.789 | 82.328 | 88.79 | 91.344 | 93.2 | 93.729 | 93.632 | 81.46 | 87.412 | 90.408 | 92.422 | 93.1 | 93 | 79.44 | 86.038 | 88.894 | 91.278 | 92.026 | 92.06
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN325KA03E | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SANYO-ELECTRIC-CO-LTD-OF-PANASONIC-GROUP-VBHN325KA03E-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN325SA17E | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SANYO-ELECTRIC-CO-LTD-OF-PANASONIC-GROUP-VBHN325SA17E-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN330KA03E | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SANYO-ELECTRIC-CO-LTD-OF-PANASONIC-GROUP-VBHN330KA03E-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.498 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN330SA17E | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SANYO-ELECTRIC-CO-LTD-OF-PANASONIC-GROUP-VBHN330SA17E-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
Schneider Electric Solar Inverters USA, Inc. | Conext CL125 | PV Inverter | 860 | 945 | 1200 | 600 | 125 | CEC Inverter Database | 600V | Schneider-Electric-Solar-Inverters-USA,-Inc.-Conext-CL125-600V | Y | 5.59 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5868 | 98.8265 | 98.8839 | 98.6821 | 98.446 | 98.2553 | 98.2894 | 98.5842 | 98.5889 | 98.4931 | 98.3594 | 98.1067 | 98.0841 | 98.4259 | 98.4773 | 98.3848 | 98.097 | 97.626
Schneider Electric Solar Inverters USA, Inc. | CS1666-1-NA | PV Inverter | 856 | 1024 | 1200 | 575 | 1666 | CEC Inverter Database | 575V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS1666-1-NA-575V | Y | 295 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44
Schneider Electric Solar Inverters USA, Inc. | CS1666-2-NA | PV Inverter | 856 | 1024 | 1200 | 575 | 1666 | CEC Inverter Database | 575V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS1666-2-NA-575V | Y | 295 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44
Schneider Electric Solar Inverters USA, Inc. | CS1666-3-NA | PV Inverter | 856 | 1024 | 1200 | 575 | 1666 | CEC Inverter Database | 575V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS1666-3-NA-575V | Y | 295 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44
Schneider Electric Solar Inverters USA, Inc. | CS1800-NA | PV Inverter | 856 | 1024 | 1200 | 575 | 1800 | CEC Inverter Database | 575V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS1800-NA-575V | Y | 295 | 180 | 360 | 540 | 900 | 1350 | 1800 | 96.89 | 97.93 | 98.08 | 98.11 | 97.92 | 97.47 | 96.67 | 97.74 | 98 | 97.99 | 97.8 | 97.45 | 95.89 | 97.43 | 97.67 | 97.87 | 97.7 | 97.34
Schneider Electric Solar Inverters USA, Inc. | CS2000-NA | PV Inverter | 865 | 1042 | 1195 | 575 | 2000 | CEC Inverter Database | 575V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS2000-NA-575V | Y | 295 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 96.76 | 97.71 | 97.98 | 97.96 | 97.66 | 97.21 | 96.32 | 97.58 | 97.87 | 97.83 | 97.56 | 97.15 | 95.92 | 97.38 | 97.69 | 97.72 | 97.5 | 97.06
Schneider Electric Solar Inverters USA, Inc. | CS2200-NA | PV Inverter | 905 | 1054 | 1200 | 600 | 2200 | CEC Inverter Database | 600V | Schneider-Electric-Solar-Inverters-USA,-Inc.-CS2200-NA-600V | Y | 295 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.9 | 98.28 | 98.33 | 98.2 | 97.82 | 97.24 | 97.6 | 98.1 | 98.19 | 98.09 | 97.72 | 97.17 | 97.21 | 97.9 | 98.05 | 97.99 | 97.65 | 97.1
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3000TL-XH-US | PV Inverter | 125 | 380 | 480 | 208 | 2.626 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3000TL-XH-US-208V | Y | 1.576 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3000TL BL-US | PV Inverter | 150 | 380 | 480 | 240 | 2.934 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3000TL-BL-US-240V | Y | 15.128 | 0.29344 | 0.58687 | 0.88031 | 1.4672 | 2.2008 | 2.9344 | 83.5494 | 88.742 | 91.5187 | 93.466 | 94.3778 | 94.5735 | 82.9531 | 88.9774 | 91.284 | 94.7821 | 95.7609 | 95.9493 | 81.2489 | 86.9992 | 91.7283 | 93.6156 | 94.9487 | 95.5889
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3000TL BL-US | PV Inverter | 150 | 380 | 480 | 208 | 2.999 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3000TL-BL-US-208V | Y | 15.128 | 0.29986 | 0.59972 | 0.89958 | 1.4993 | 2.249 | 2.9986 | 83.2934 | 88.7087 | 91.2183 | 93.3997 | 94.3355 | 94.6645 | 83.5823 | 88.3477 | 91.9042 | 94.2283 | 95.3991 | 95.8876 | 82.5038 | 87.6858 | 91.4301 | 93.8779 | 94.8499 | 95.7624
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3000TL-XH-US | PV Inverter | 125 | 380 | 480 | 240 | 3.095 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3000TL-XH-US-240V | Y | 1.593 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3800TL-XH-US | PV Inverter | 160 | 380 | 480 | 208 | 3.324 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3800TL-XH-US-208V | Y | 1.576 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3600TL BL-US | PV Inverter | 150 | 380 | 480 | 208 | 3.581 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3600TL-BL-US-208V | Y | 15.128 | 0.3581 | 0.7162 | 1.0743 | 1.7905 | 2.6858 | 3.581 | 84.9552 | 90.4271 | 92.825 | 93.7968 | 94.5716 | 94.4365 | 85.0401 | 90.7332 | 93.4293 | 94.4908 | 95.7747 | 96.2727 | 82.3717 | 88.9668 | 92.9784 | 94.2953 | 95.7884 | 95.6672
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3600TL BL-US | PV Inverter | 150 | 380 | 480 | 240 | 3.608 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3600TL-BL-US-240V | Y | 15.128 | 0.36084 | 0.72167 | 1.0825 | 1.8042 | 2.7063 | 3.6084 | 84.9226 | 90.0495 | 92.9079 | 93.7875 | 94.4318 | 94.456 | 84.8681 | 90.93 | 93.8567 | 94.562 | 95.5583 | 95.9727 | 82.4977 | 88.9887 | 92.2935 | 94.4687 | 94.7381 | 95.6144
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 4000MTLP-US | PV Inverter | 100 | 482 | 550 | 208 | 3.62 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-4000MTLP-US-208V | Y | 0.05 | 0.36 | 0.72 | 1.08 | 1.81 | 2.71 | 3.62 | 88.8 | 91.7 | 93.1 | 94.6 | 95.2 | 95.2 | 92.2 | 95.7 | 95.7 | 96.5 | 96.7 | 96.7 | 91.4 | 94.3 | 95.3 | 96.2 | 96.5 | 96.6
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3800TL-XH-US | PV Inverter | 160 | 380 | 480 | 240 | 3.888 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3800TL-XH-US-240V | Y | 1.593 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4000TL BL-US | PV Inverter | 180 | 380 | 480 | 240 | 3.988 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4000TL-BL-US-240V | Y | 15.128 | 0.39884 | 0.79767 | 1.1965 | 1.9942 | 2.9913 | 3.9884 | 86.9226 | 91.0495 | 92.9079 | 94.5875 | 95.1318 | 95.156 | 86.5681 | 92.23 | 94.3567 | 95.662 | 96.2583 | 96.1727 | 84.4977 | 91.0887 | 93.3935 | 95.1687 | 96.1381 | 96.0144
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4000TL BL-US | PV Inverter | 150 | 380 | 480 | 208 | 4.004 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4000TL-BL-US-208V | Y | 15.128 | 0.4004 | 0.8008 | 1.2012 | 2.002 | 3.003 | 4.004 | 86.7552 | 91.4271 | 93.125 | 94.3968 | 94.9716 | 95.2365 | 86.8401 | 92.1332 | 94.3293 | 95.6908 | 96.1747 | 96.1727 | 84.8717 | 91.2668 | 93.5784 | 95.1953 | 96.0884 | 96.0672
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 4000MTLP-US | PV Inverter | 100 | 482 | 550 | 240 | 4.05 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-4000MTLP-US-240V | Y | 0.05 | 0.4 | 0.81 | 1.21 | 2.02 | 3.04 | 4.05 | 89.5 | 92.1 | 93.7 | 95 | 95.5 | 95.6 | 93.1 | 95.4 | 96.2 | 96.9 | 97.1 | 97.1 | 92.3 | 94.8 | 95.9 | 96.6 | 96.9 | 97
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 4000MTLP-US | PV Inverter | 100 | 482 | 550 | 277 | 4.06 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-4000MTLP-US-277V | Y | 0.05 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.06 | 88.3 | 91.5 | 93.1 | 94.6 | 95.3 | 95.5 | 93.6 | 95.7 | 96.6 | 95.3 | 97.4 | 97.4 | 92.7 | 95.1 | 96.3 | 96.9 | 97.2 | 97.3
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 5000TL-XH-US | PV Inverter | 210 | 380 | 480 | 208 | 4.28 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-5000TL-XH-US-208V | Y | 1.576 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 5000MTLP-US | PV Inverter | 100 | 482 | 550 | 208 | 4.59 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-5000MTLP-US-208V | Y | 0.05 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 89.9 | 92.5 | 93.8 | 94.9 | 95.1 | 95.1 | 93.2 | 95.3 | 96 | 96.6 | 96.7 | 96.6 | 92.5 | 94.8 | 95.7 | 96.4 | 96.6 | 96.5
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4600TL BL-US | PV Inverter | 180 | 380 | 480 | 240 | 4.598 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4600TL-BL-US-240V | Y | 15.128 | 0.45977 | 0.91955 | 1.3793 | 2.2989 | 3.4483 | 4.5977 | 86.9226 | 92.0495 | 93.3079 | 94.9095 | 95.2538 | 95.188 | 86.8681 | 92.43 | 94.5567 | 95.897 | 96.2323 | 96.2077 | 85.4977 | 91.4887 | 93.6035 | 95.4327 | 96.2821 | 96.1164
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4600TL BL-US | PV Inverter | 180 | 380 | 480 | 208 | 4.604 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4600TL-BL-US-208V | Y | 15.128 | 0.4604 | 0.9208 | 1.3812 | 2.302 | 3.453 | 4.604 | 86.7552 | 91.6271 | 93.425 | 94.7968 | 95.1716 | 95.2365 | 87.8401 | 92.8332 | 94.7293 | 95.7908 | 96.2747 | 96.2727 | 85.8717 | 92.5668 | 94.0784 | 95.2953 | 96.3884 | 96.2672
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 5000TL-XH-US | PV Inverter | 210 | 380 | 480 | 240 | 4.943 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-5000TL-XH-US-240V | Y | 1.593 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 5000TL BL-US | PV Inverter | 230 | 380 | 480 | 240 | 4.954 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-5000TL-BL-US-240V | Y | 15.128 | 0.49537 | 0.99073 | 1.4861 | 2.4768 | 3.7153 | 4.9537 | 88.2674 | 92.0279 | 93.9177 | 95.1688 | 95.5976 | 95.4626 | 88.8274 | 93.6476 | 94.5929 | 96.1977 | 96.5262 | 95.9757 | 86.6548 | 92.4155 | 93.7005 | 95.5802 | 96.117 | 96.1089
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 5000TL BL-US | PV Inverter | 230 | 380 | 480 | 208 | 4.969 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-5000TL-BL-US-208V | Y | 15.128 | 0.49688 | 0.99376 | 1.4906 | 2.4844 | 3.7266 | 4.9688 | 87.9969 | 91.8291 | 94.0292 | 95.277 | 95.6685 | 95.4968 | 88.6415 | 93.5556 | 94.7545 | 95.9536 | 96.5989 | 96.0872 | 87.0137 | 92.8034 | 93.5434 | 96.1629 | 96.0924 | 96.1985
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 5000MTLP-US | PV Inverter | 100 | 482 | 550 | 277 | 5.06 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-5000MTLP-US-277V | Y | 0.05 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 89.5 | 92.3 | 93.8 | 95 | 95.5 | 95.5 | 94.3 | 96.1 | 96.8 | 97.3 | 97.4 | 97.3 | 93.5 | 95.6 | 96.4 | 97 | 97.2 | 97.2
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 5000MTLP-US | PV Inverter | 100 | 482 | 550 | 240 | 5.07 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-5000MTLP-US-240V | Y | 0.05 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.07 | 90.5 | 93 | 94.3 | 95.2 | 95.4 | 95.3 | 93.9 | 95.8 | 96.5 | 97 | 97.1 | 96.9 | 93.1 | 95.3 | 96.1 | 96.8 | 96.9 | 96.9
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 6000TL-XH-US | PV Inverter | 170 | 380 | 480 | 208 | 5.143 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-6000TL-XH-US-208V | Y | 1.576 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 6000TL BL-US | PV Inverter | 230 | 380 | 480 | 208 | 5.232 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-6000TL-BL-US-208V | Y | 15.128 | 0.52322 | 1.0464 | 1.5697 | 2.6161 | 3.9242 | 5.2322 | 91.6216 | 94.3804 | 95.004 | 95.6415 | 95.648 | 95.6498 | 94.0058 | 96.3321 | 96.66 | 96.8442 | 96.8058 | 96.5216 | 93.9666 | 96.0001 | 96.4128 | 96.8643 | 96.7314 | 96.4957
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 6000MTLP-US | PV Inverter | 100 | 482 | 550 | 208 | 5.34 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-6000MTLP-US-208V | Y | 0.05 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.34 | 90.7 | 93.2 | 94.3 | 95 | 95 | 94.9 | 93.9 | 95.7 | 96.3 | 96.7 | 96.6 | 96.4 | 93.3 | 95.3 | 95.9 | 96.5 | 96.5 | 96.3
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 6000TL BL-US | PV Inverter | 230 | 380 | 480 | 240 | 5.864 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-6000TL-BL-US-240V | Y | 15.128 | 0.58643 | 1.1729 | 1.7593 | 2.9322 | 4.3982 | 5.8643 | 91.5816 | 94.3604 | 94.954 | 95.5915 | 95.628 | 95.6398 | 93.9658 | 96.3021 | 96.58 | 96.8142 | 96.7558 | 96.5216 | 93.9266 | 95.9701 | 96.3828 | 96.8343 | 96.7114 | 96.4757
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 6000TL-XH-US | PV Inverter | 170 | 380 | 480 | 240 | 5.918 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-6000TL-XH-US-240V | Y | 1.593 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 6000MTLP-US | PV Inverter | 100 | 482 | 550 | 240 | 6.08 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-6000MTLP-US-240V | Y | 0.05 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 91.3 | 93.6 | 94.7 | 95.4 | 95.5 | 95.6 | 94.6 | 96.1 | 96.7 | 97 | 97 | 96.8 | 93.9 | 95.6 | 96.3 | 96.8 | 96.8 | 96.7
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 6000MTLP-US | PV Inverter | 100 | 482 | 550 | 277 | 6.08 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-6000MTLP-US-277V | Y | 0.05 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 90.4 | 93 | 94.4 | 95.3 | 95.4 | 95.3 | 94.9 | 96.4 | 96.9 | 97.3 | 97.4 | 97.2 | 94.1 | 95.9 | 96.6 | 97.1 | 97.2 | 97.1
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7000MTLP-US | PV Inverter | 280 | 385 | 485 | 208 | 6.093 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7000MTLP-US-208V | Y | 0.05 | 0.6093 | 1.2186 | 1.8279 | 3.0465 | 4.5697 | 6.093 | 93.9 | 95.4 | 95.8 | 95.9 | 95.5 | 95.3 | 95.4 | 96.6 | 96.8 | 96.6 | 96.1 | 95.9 | 94.3 | 95.9 | 96.4 | 96.5 | 96.2 | 96 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 7600TL-XH-US | PV Inverter | 212 | 380 | 480 | 208 | 6.58 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-7600TL-XH-US-208V | Y | 1.576 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7600MTLP-US | PV Inverter | 270 | 380 | 480 | 208 | 6.741 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7600MTLP-US-208V | Y | 0.05 | 0.6741 | 1.3482 | 2.0223 | 3.3705 | 5.0558 | 6.741 | 94.1 | 95.5 | 95.7 | 95.7 | 95.2 | 95 | 95.7 | 96.7 | 96.8 | 96.6 | 96.1 | 95.9 | 94.7 | 96.2 | 96.5 | 96.5 | 96.1 | 95.8 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7000MTLP-US | PV Inverter | 270 | 385 | 485 | 240 | 7.011 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7000MTLP-US-240V | Y | 0.051 | 0.70111 | 1.4022 | 2.1033 | 3.5056 | 5.2583 | 7.0111 | 94 | 95.7 | 95.9 | 96 | 95.8 | 95.5 | 95.7 | 96.8 | 97 | 96.9 | 96.7 | 96.4 | 94.6 | 96.4 | 96.8 | 96.9 | 96.7 | 96.3 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7000MTLP-US | PV Inverter | 275 | 385 | 480 | 277 | 7.0161 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7000MTLP-US-277V | Y | 0.051 | 0.70161 | 1.4032 | 2.1048 | 3.508 | 5.2621 | 7.0161 | 92.8 | 95.2 | 95.4 | 95.9 | 96.1 | 95.9 | 93.6 | 96.3 | 96.7 | 96.9 | 96.8 | 96.5 | 95 | 96.6 | 97.1 | 97.3 | 97.2 | 97 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 8000MTLP-US | PV Inverter | 330 | 480 | 550 | 208 | 7.107 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-8000MTLP-US-208V | Y | 3.3 | 0.7107 | 1.4214 | 2.1321 | 3.5535 | 5.3303 | 7.107 | 95.2319 | 96.8981 | 97.1668 | 97.2152 | 96.9406 | 96.7327 | 95.3248 | 96.8981 | 97.3535 | 97.5256 | 97.3657 | 97.2044 | 94.5675 | 96.5387 | 97.0783 | 97.371 | 97.2917 | 97.1309
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US | PV Inverter | 250 | 380 | 480 | 208 | 7.166 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-8200TL-XH-US-208V | Y | 10 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 7600TL-XH-US | PV Inverter | 212 | 380 | 480 | 240 | 7.524 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-7600TL-XH-US-240V | Y | 1.593 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7600MTLP-US | PV Inverter | 270 | 380 | 480 | 240 | 7.604 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7600MTLP-US-240V | Y | 0.051 | 0.7604 | 1.5208 | 2.2812 | 3.802 | 5.703 | 7.604 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 7600MTLP-US | PV Inverter | 270 | 380 | 480 | 277 | 7.652 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-7600MTLP-US-277V | Y | 0.051 | 0.76515 | 1.5303 | 2.2954 | 3.8258 | 5.7386 | 7.6515 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 |  | Original power level values incorrectly in Watts (W); converted to kiloWatts (kW)
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 9000MTLP-US | PV Inverter | 330 | 480 | 550 | 208 | 7.864 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-9000MTLP-US-208V | Y | 3.3 | 0.7864 | 1.5728 | 2.3592 | 3.932 | 5.898 | 7.864 | 95.4343 | 96.8634 | 97.1228 | 97.0837 | 96.7601 | 96.5393 | 95.5184 | 96.9899 | 97.3531 | 97.4463 | 97.1787 | 97.0001 | 94.827 | 96.6169 | 97.0564 | 97.2473 | 97.0819 | 96.8936
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US | PV Inverter | 250 | 380 | 480 | 208 | 7.874 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-9000TL-XH-US-208V | Y | 10 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 8000MTLP-US | PV Inverter | 330 | 480 | 550 | 240 | 8.061 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-8000MTLP-US-240V | Y | 3.5 | 0.8061 | 1.6122 | 2.4183 | 4.0305 | 6.0457 | 8.061 | 95.4816 | 96.806 | 97.2982 | 97.458 | 97.318 | 97.0166 | 95.7939 | 97.0913 | 97.5954 | 97.859 | 97.7928 | 97.5766 | 95.2637 | 96.7576 | 97.3124 | 97.6341 | 97.6942 | 97.5279
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 8000MTLP-US | PV Inverter | 330 | 480 | 550 | 277 | 8.137 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-8000MTLP-US-277V | Y | 3.7 | 0.8137 | 1.6274 | 2.4411 | 4.0685 | 6.1028 | 8.137 | 95.4421 | 96.6109 | 97.1824 | 97.5198 | 97.4925 | 97.2428 | 96.2697 | 97.2044 | 97.777 | 98.0996 | 98.0984 | 97.9494 | 95.8631 | 96.8898 | 97.4879 | 97.8391 | 97.9642 | 97.8946
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US | PV Inverter | 250 | 380 | 480 | 240 | 8.251 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-8200TL-XH-US-240V | Y | 10 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 10000MTLP-US | PV Inverter | 330 | 480 | 550 | 208 | 8.63 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-10000MTLP-US-208V | Y | 3.3 | 0.863 | 1.726 | 2.589 | 4.315 | 6.4725 | 8.63 | 95.5609 | 96.3702 | 96.5193 | 97.0537 | 96.6088 | 96.4293 | 95.6227 | 96.7681 | 96.7901 | 97.4531 | 97.1269 | 96.9585 | 95.0326 | 96.7812 | 97.1518 | 97.3399 | 96.9975 | 96.8805
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US | PV Inverter | 250 | 380 | 480 | 208 | 8.76 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-10000TL-XH-US-208V | Y | 10 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 9000MTLP-US | PV Inverter | 330 | 480 | 550 | 240 | 9.061 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-9000MTLP-US-240V | Y | 3.5 | 0.9061 | 1.8122 | 2.7183 | 4.5305 | 6.7957 | 9.061 | 95.9306 | 97.0351 | 97.3624 | 97.4055 | 97.1587 | 96.7832 | 96.1264 | 97.3308 | 97.7098 | 97.8566 | 97.7061 | 97.4356 | 95.536 | 96.9828 | 97.3349 | 97.5876 | 97.5568 | 97.3138
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US | PV Inverter | 250 | 380 | 480 | 240 | 9.063 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-9000TL-XH-US-240V | Y | 10 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 9000MTLP-US | PV Inverter | 330 | 480 | 550 | 277 | 9.169 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-9000MTLP-US-277V | Y | 3.7 | 0.9169 | 1.8338 | 2.7507 | 4.5845 | 6.8768 | 9.169 | 95.6877 | 96.866 | 97.3366 | 97.5417 | 97.445 | 97.1574 | 96.3449 | 97.2806 | 97.7734 | 98.114 | 98.0647 | 97.8914 | 95.9346 | 97.0873 | 97.6193 | 97.9244 | 98.0003 | 97.8943
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US | PV Inverter | 250 | 380 | 480 | 208 | 10.04 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-11400TL-XH-US-208V | Y | 10 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 10000MTLP-US | PV Inverter | 330 | 480 | 550 | 240 | 10.058 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-10000MTLP-US-240V | Y | 3.5 | 1.0058 | 2.0116 | 3.0174 | 5.029 | 7.5435 | 10.058 | 95.7496 | 96.5751 | 96.6916 | 96.5323 | 96.917 | 96.6087 | 95.8602 | 96.9019 | 97.0339 | 97.0528 | 97.6148 | 97.3005 | 95.3753 | 96.9373 | 97.3973 | 97.6401 | 97.5368 | 97.2343
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US | PV Inverter | 250 | 380 | 480 | 240 | 10.082 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-10000TL-XH-US-240V | Y | 10 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 10000MTLP-US | PV Inverter | 330 | 480 | 550 | 277 | 10.165 | CEC Inverter Database | 277V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-10000MTLP-US-277V | Y | 3.7 | 1.0165 | 2.033 | 3.0495 | 5.0825 | 7.6238 | 10.165 | 95.5795 | 96.4291 | 96.9301 | 97.5168 | 97.3177 | 97.0515 | 96.0695 | 97.219 | 97.3929 | 98.1228 | 97.9602 | 97.7314 | 95.8737 | 97.1605 | 97.9253 | 97.9533 | 97.9509 | 97.7632
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US | PV Inverter | 250 | 380 | 480 | 240 | 11.52 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-11400TL-XH-US-240V | Y | 10 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 33000TL3-US | PV Inverter | 480 | 700 | 800 | 480 | 32.27 | CEC Inverter Database | 480V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-33000TL3-US-480V | Y | 2.092 | 3.23 | 6.45 | 9.68 | 16.14 | 24.2 | 32.27 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.5 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 97.5 | 98 | 98.3 | 98.5 | 98.3 | 98.1
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 36000TL3-US | PV Inverter | 520 | 700 | 800 | 480 | 35.71 | CEC Inverter Database | 480V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-36000TL3-US-480V | Y | 2.051 | 3.57 | 7.14 | 10.71 | 17.86 | 26.78 | 35.71 | 97.5 | 98.1 | 98.2 | 98.3 | 97.9 | 97.6 | 98 | 98.6 | 98.6 | 98.6 | 98.6 | 98.4 | 97.4 | 98.1 | 98.2 | 98.2 | 98.3 | 98.1
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 40000TL3-US | PV Inverter | 570 | 700 | 800 | 480 | 39.85 | CEC Inverter Database | 480V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-GROWATT-40000TL3-US-480V | Y | 2.051 | 3.98 | 7.97 | 11.95 | 19.92 | 29.89 | 39.85 | 97.5 | 98 | 98 | 98.2 | 98 | 97.6 | 98.2 | 98.6 | 98.6 | 98.4 | 98.7 | 98.5 | 97.5 | 98.1 | 98.1 | 98 | 98.3 | 98.1
SMA America | SB3.0-1SP-US-40 | PV Inverter | 155 | 365 | 480 | 208 | 3 | CEC Inverter Database | 208V | SMA-America-SB3.0-1SP-US-40-208V | Y | 5.36 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443
SMA America | SB3.0-1SP-US-40 | PV Inverter | 155 | 365 | 480 | 240 | 3 | CEC Inverter Database | 240V | SMA-America-SB3.0-1SP-US-40-240V | Y | 5.39 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008
SMA America | SB3.0-1TP-US-40 | PV Inverter | 155 | 365 | 480 | 208 | 3 | CEC Inverter Database | 208V | SMA-America-SB3.0-1TP-US-40-208V | Y | 5.36 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443
SMA America | SB3.0-1TP-US-40 | PV Inverter | 155 | 365 | 480 | 240 | 3 | CEC Inverter Database | 240V | SMA-America-SB3.0-1TP-US-40-240V | Y | 5.39 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008
SMA America | SB3.0-1SP-US-41 | PV Inverter | 155 | 365 | 480 | 208 | 3.0276 | CEC Inverter Database | 208V | SMA-America-SB3.0-1SP-US-41-208V | Y | 5.36 | 0.30276 | 0.60552 | 0.90828 | 1.5138 | 2.2707 | 3.0276 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443
SMA America | SB3.0-1TP-US-41 | PV Inverter | 155 | 365 | 480 | 208 | 3.028 | CEC Inverter Database | 208V | SMA-America-SB3.0-1TP-US-41-208V | Y | 5.36 | 0.303 | 0.606 | 0.908 | 1.514 | 2.271 | 3.028 | 92.08 | 94.91 | 95.63 | 95.99 | 96 | 95.73 | 92.07 | 95.66 | 96.46 | 97.04 | 97.2 | 97.08 | 88.52 | 94.5 | 95.72 | 96.42 | 96.77 | 96.64
SMA America | SB3.0-1SP-US-41 | PV Inverter | 155 | 365 | 480 | 240 | 3.036 | CEC Inverter Database | 240V | SMA-America-SB3.0-1SP-US-41-240V | Y | 5.39 | 0.30362 | 0.60724 | 0.91086 | 1.5181 | 2.2771 | 3.0362 | 90.952 | 94.442 | 95.38 | 95.94 | 96.038 | 95.94 | 92.036 | 95.788 | 96.642 | 97.166 | 97.516 | 97.58 | 88.51 | 94.438 | 95.738 | 96.678 | 97.024 | 97
SMA America | SB3.0-1TP-US-41 | PV Inverter | 155 | 365 | 480 | 240 | 3.036 | CEC Inverter Database | 240V | SMA-America-SB3.0-1TP-US-41-240V | Y | 5.39 | 0.304 | 0.607 | 0.911 | 1.518 | 2.277 | 3.036 | 90.95 | 94.44 | 95.38 | 95.94 | 96.04 | 95.94 | 92.04 | 95.79 | 96.64 | 97.17 | 97.52 | 97.58 | 88.51 | 94.44 | 95.74 | 96.68 | 97.02 | 97
SMA America | SB3.8-1SP-US-40 | PV Inverter | 195 | 365 | 480 | 208 | 3.6 | CEC Inverter Database | 208V | SMA-America-SB3.8-1SP-US-40-208V | Y | 5.36 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496
SMA America | SB3.8-1TP-US-40 | PV Inverter | 195 | 365 | 480 | 208 | 3.6 | CEC Inverter Database | 208V | SMA-America-SB3.8-1TP-US-40-208V | Y | 5.36 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496
SMA America | SB3.8-1SP-US-41 | PV Inverter | 195 | 365 | 480 | 208 | 3.604 | CEC Inverter Database | 208V | SMA-America-SB3.8-1SP-US-41-208V | Y | 5.36 | 0.36039 | 0.72079 | 1.0812 | 1.802 | 2.7029 | 3.6039 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496
SMA America | SB3.8-1TP-US-41 | PV Inverter | 195 | 365 | 480 | 208 | 3.604 | CEC Inverter Database | 208V | SMA-America-SB3.8-1TP-US-41-208V | Y | 5.36 | 0.36 | 0.721 | 1.081 | 1.802 | 2.703 | 3.604 | 92.93 | 95.48 | 96.03 | 96.47 | 96.38 | 96.15 | 92.53 | 95.95 | 96.62 | 97.06 | 97.22 | 96.98 | 89.81 | 96.92 | 96 | 96.58 | 96.77 | 96.85
SMA America | SB3.8-1SP-US-40 | PV Inverter | 195 | 365 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | SMA-America-SB3.8-1SP-US-40-240V | Y | 5.39 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074
SMA America | SB3.8-1TP-US-40 | PV Inverter | 195 | 365 | 480 | 240 | 3.8 | CEC Inverter Database | 240V | SMA-America-SB3.8-1TP-US-40-240V | Y | 5.39 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074
SMA America | SB3.8-1SP-US-41 | PV Inverter | 195 | 365 | 480 | 240 | 3.853 | CEC Inverter Database | 240V | SMA-America-SB3.8-1SP-US-41-240V | Y | 5.39 | 0.38532 | 0.77064 | 1.156 | 1.9266 | 2.8899 | 3.8532 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074
SMA America | SB3.8-1TP-US-41 | PV Inverter | 195 | 365 | 480 | 240 | 3.853 | CEC Inverter Database | 240V | SMA-America-SB3.8-1TP-US-41-240V | Y | 5.39 | 0.385 | 0.771 | 1.156 | 1.927 | 2.89 | 3.853 | 92.68 | 95.37 | 96.07 | 96.46 | 96.44 | 96.23 | 93.68 | 96.44 | 96.9 | 97.43 | 97.59 | 97.47 | 90.81 | 95.31 | 96.4 | 96.91 | 97.16 | 97.31
SMA America | SB5.0-1SP-US-40 | PV Inverter | 220 | 365 | 480 | 208 | 5 | CEC Inverter Database | 208V | SMA-America-SB5.0-1SP-US-40-208V | Y | 5.06 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8
SMA America | SB5.0-1SP-US-40 | PV Inverter | 220 | 365 | 480 | 240 | 5 | CEC Inverter Database | 240V | SMA-America-SB5.0-1SP-US-40-240V | Y | 5.21 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3
SMA America | SB5.0-1TP-US-40 | PV Inverter | 220 | 365 | 480 | 208 | 5 | CEC Inverter Database | 208V | SMA-America-SB5.0-1TP-US-40-208V | Y | 5.06 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8
SMA America | SB5.0-1TP-US-40 | PV Inverter | 220 | 365 | 480 | 240 | 5 | CEC Inverter Database | 240V | SMA-America-SB5.0-1TP-US-40-240V | Y | 5.21 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3
SMA America | SB5.0-1SP-US-41 | PV Inverter | 220 | 365 | 480 | 208 | 5.05 | CEC Inverter Database | 208V | SMA-America-SB5.0-1SP-US-41-208V | Y | 5.06 | 0.50499 | 1.01 | 1.515 | 2.5249 | 3.7874 | 5.0499 | 94.6943 | 96.3064 | 96.5562 | 96.6291 | 96.4459 | 96.0274 | 94.7254 | 96.7172 | 97.0771 | 97.2289 | 97.0843 | 96.7747 | 91.1032 | 96.149 | 96.6625 | 96.912 | 96.9618 | 96.7967
SMA America | SB5.0-1TP-US-41 | PV Inverter | 220 | 365 | 480 | 208 | 5.05 | CEC Inverter Database | 208V | SMA-America-SB5.0-1TP-US-41-208V | Y | 5.06 | 0.50499 | 1.01 | 1.515 | 2.5249 | 3.7874 | 5.0499 | 94.6943 | 96.3064 | 96.5562 | 96.6291 | 96.4459 | 96.0274 | 94.7254 | 96.7172 | 97.0771 | 97.2289 | 97.0843 | 96.7747 | 91.1032 | 96.149 | 96.6625 | 96.912 | 96.9618 | 96.7967
SMA America | SB5.0-1SP-US-41 | PV Inverter | 220 | 365 | 480 | 240 | 5.059 | CEC Inverter Database | 240V | SMA-America-SB5.0-1SP-US-41-240V | Y | 5.21 | 0.50586 | 1.0117 | 1.5176 | 2.5293 | 3.794 | 5.0586 | 93.3494 | 96.0308 | 96.4559 | 96.6614 | 96.6099 | 96.3678 | 93.4405 | 96.8585 | 97.2319 | 97.5098 | 97.4129 | 97.2237 | 91.21 | 96.1804 | 96.8054 | 97.2068 | 97.3728 | 97.27
SMA America | SB5.0-1TP-US-41 | PV Inverter | 220 | 365 | 480 | 240 | 5.059 | CEC Inverter Database | 240V | SMA-America-SB5.0-1TP-US-41-240V | Y | 5.21 | 0.50586 | 1.0117 | 1.5176 | 2.5293 | 3.794 | 5.0586 | 93.3494 | 96.0308 | 96.4559 | 96.6614 | 96.6099 | 96.3678 | 93.4405 | 96.8585 | 97.2319 | 97.5098 | 97.4129 | 97.2237 | 91.21 | 96.1804 | 96.8054 | 97.2068 | 97.3728 | 97.27
SMA America | SB6.0-1SP-US-41 | PV Inverter | 220 | 365 | 480 | 208 | 5.418 | CEC Inverter Database | 208V | SMA-America-SB6.0-1SP-US-41-208V | Y | 5.06 | 0.54177 | 1.0835 | 1.6253 | 2.7088 | 4.0633 | 5.4177 | 94.8098 | 96.3223 | 96.5669 | 96.627 | 96.4299 | 95.9837 | 94.8499 | 96.7381 | 97.0781 | 97.2314 | 97.0698 | 96.7747 | 91.7463 | 96.1806 | 96.6775 | 96.8453 | 96.9618 | 96.786
SMA America | SB6.0-1TP-US-41 | PV Inverter | 220 | 365 | 480 | 208 | 5.418 | CEC Inverter Database | 208V | SMA-America-SB6.0-1TP-US-41-208V | Y | 5.06 | 0.54177 | 1.0835 | 1.6253 | 2.7088 | 4.0633 | 5.4177 | 94.8098 | 96.3223 | 96.5669 | 96.627 | 96.4299 | 95.9837 | 94.8499 | 96.7381 | 97.0781 | 97.2314 | 97.0698 | 96.7747 | 91.7463 | 96.1806 | 96.6775 | 96.8453 | 96.9618 | 96.786
SMA America | SB6.0-1SP-US-40 | PV Inverter | 220 | 365 | 480 | 208 | 5.49 | CEC Inverter Database | 208V | SMA-America-SB6.0-1SP-US-40-208V | Y | 5.06 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8
SMA America | SB6.0-1TP-US-40 | PV Inverter | 220 | 365 | 480 | 208 | 5.49 | CEC Inverter Database | 208V | SMA-America-SB6.0-1TP-US-40-208V | Y | 5.06 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8
SMA America | SB6.0-1SP-US-40 | PV Inverter | 220 | 365 | 480 | 240 | 6 | CEC Inverter Database | 240V | SMA-America-SB6.0-1SP-US-40-240V | Y | 5.21 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97
SMA America | SB6.0-1TP-US-40 | PV Inverter | 220 | 365 | 480 | 240 | 6 | CEC Inverter Database | 240V | SMA-America-SB6.0-1TP-US-40-240V | Y | 5.21 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97
SMA America | SB6.0-1SP-US-41 | PV Inverter | 220 | 365 | 480 | 240 | 6.052 | CEC Inverter Database | 240V | SMA-America-SB6.0-1SP-US-41-240V | Y | 5.21 | 0.60518 | 1.2104 | 1.8155 | 3.0259 | 4.5389 | 6.0518 | 94.6792 | 96.3065 | 96.6157 | 96.6489 | 96.481 | 96.137 | 95.4374 | 97.1021 | 97.3736 | 97.5643 | 97.3124 | 97.0135 | 93.3743 | 96.5451 | 97.0147 | 97.3236 | 97.2821 | 97.0129
SMA America | SB6.0-1TP-US-41 | PV Inverter | 220 | 365 | 480 | 240 | 6.052 | CEC Inverter Database | 240V | SMA-America-SB6.0-1TP-US-41-240V | Y | 5.21 | 0.60518 | 1.2104 | 1.8155 | 3.0259 | 4.5389 | 6.0518 | 94.6792 | 96.3065 | 96.6157 | 96.6489 | 96.481 | 96.137 | 95.4374 | 97.1021 | 97.3736 | 97.5643 | 97.3124 | 97.0135 | 93.3743 | 96.5451 | 97.0147 | 97.3236 | 97.2821 | 97.0129
SMA America | SB7.0-1SP-US-40 | PV Inverter | 245 | 365 | 480 | 208 | 6.92 | CEC Inverter Database | 208V | SMA-America-SB7.0-1SP-US-40-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.0-1TP-US-40 | PV Inverter | 245 | 365 | 480 | 208 | 6.92 | CEC Inverter Database | 208V | SMA-America-SB7.0-1TP-US-40-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.7-1SP-US-40 | PV Inverter | 270 | 365 | 480 | 208 | 6.92 | CEC Inverter Database | 208V | SMA-America-SB7.7-1SP-US-40-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.7-1TP-US-40 | PV Inverter | 270 | 365 | 480 | 208 | 6.92 | CEC Inverter Database | 208V | SMA-America-SB7.7-1TP-US-40-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.0-1SP-US-41 | PV Inverter | 245 | 365 | 480 | 208 | 6.923 | CEC Inverter Database | 208V | SMA-America-SB7.0-1SP-US-41-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.0-1TP-US-41 | PV Inverter | 245 | 365 | 480 | 208 | 6.923 | CEC Inverter Database | 208V | SMA-America-SB7.0-1TP-US-41-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.7-1SP-US-41 | PV Inverter | 270 | 365 | 480 | 208 | 6.923 | CEC Inverter Database | 208V | SMA-America-SB7.7-1SP-US-41-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.7-1TP-US-41 | PV Inverter | 270 | 365 | 480 | 208 | 6.923 | CEC Inverter Database | 208V | SMA-America-SB7.7-1TP-US-41-208V | Y | 5.37 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048
SMA America | SB7.0-1SP-US-40 | PV Inverter | 245 | 365 | 480 | 240 | 7 | CEC Inverter Database | 240V | SMA-America-SB7.0-1SP-US-40-240V | Y | 5.1 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677
SMA America | SB7.0-1TP-US-40 | PV Inverter | 245 | 365 | 480 | 240 | 7 | CEC Inverter Database | 240V | SMA-America-SB7.0-1TP-US-40-240V | Y | 5.1 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677
SMA America | SB7.0-1SP-US-41 | PV Inverter | 245 | 365 | 480 | 240 | 7.009 | CEC Inverter Database | 240V | SMA-America-SB7.0-1SP-US-41-240V | Y | 5.1 | 0.70094 | 1.4019 | 2.1028 | 3.5047 | 5.257 | 7.0094 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677
SMA America | SB7.0-1TP-US-41 | PV Inverter | 245 | 365 | 480 | 240 | 7.009 | CEC Inverter Database | 240V | SMA-America-SB7.0-1TP-US-41-240V | Y | 5.1 | 0.70094 | 1.4019 | 2.1028 | 3.5047 | 5.257 | 7.0094 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677
SMA America | SB7.7-1SP-US-41 | PV Inverter | 270 | 365 | 480 | 240 | 7.756 | CEC Inverter Database | 240V | SMA-America-SB7.7-1SP-US-41-240V | Y | 5.1 | 0.77564 | 1.5513 | 2.3269 | 3.8782 | 5.8173 | 7.7564 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284
SMA America | SB7.7-1TP-US-41 | PV Inverter | 270 | 365 | 480 | 240 | 7.756 | CEC Inverter Database | 240V | SMA-America-SB7.7-1TP-US-41-240V | Y | 5.1 | 0.77564 | 1.5513 | 2.3269 | 3.8782 | 5.8173 | 7.7564 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284
SMA America | SB7.7-1SP-US-40 | PV Inverter | 270 | 365 | 480 | 240 | 7.76 | CEC Inverter Database | 240V | SMA-America-SB7.7-1SP-US-40-240V | Y | 5.1 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284
SMA America | SB7.7-1TP-US-40 | PV Inverter | 270 | 365 | 480 | 240 | 7.76 | CEC Inverter Database | 240V | SMA-America-SB7.7-1TP-US-40-240V | Y | 5.1 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284
SMA America | STP12000TL-US-10 | PV Inverter | 300 | 675 | 800 | 480 | 12 | CEC Inverter Database | 480V | SMA-America-STP12000TL-US-10-480V | Y | 1.79 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898
SMA America | STP15000TL-US-10 | PV Inverter | 300 | 675 | 800 | 480 | 15 | CEC Inverter Database | 480V | SMA-America-STP15000TL-US-10-480V | Y | 1.79 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572
SMA America | STP20000TL-US-10 | PV Inverter | 380 | 695 | 800 | 480 | 20 | CEC Inverter Database | 480V | SMA-America-STP20000TL-US-10-480V | Y | 1.79 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422
SMA America | STP24000TL-US-10 | PV Inverter | 450 | 712 | 800 | 480 | 24 | CEC Inverter Database | 480V | SMA-America-STP24000TL-US-10-480V | Y | 1.79 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823
SMA America | STP30000TL-US-10 | PV Inverter | 500 | 720 | 800 | 480 | 30 | CEC Inverter Database | 480V | SMA-America-STP30000TL-US-10-480V | Y | 1.22 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08
SMA America | STP 33-US-41 | PV Inverter | 330 | 683 | 800 | 480 | 33.3 | CEC Inverter Database | 480V | SMA-America-STP-33-US-41-480V | Y | 5.43 | 3.33 | 6.66 | 9.99 | 16.65 | 24.975 | 33.3 | 94.259 | 96.337 | 96.705 | 96.644 | 96.46 | 96.003 | 94.707 | 96.755 | 97.303 | 97.647 | 97.694 | 97.719 | 95.731 | 97.626 | 98.044 | 98.229 | 98.119 | 97.988
SMA America | STP 50-US-41 | PV Inverter | 500 | 725 | 800 | 480 | 50 | CEC Inverter Database | 480V | SMA-America-STP-50-US-41-480V | Y | 5.43 | 5.0006 | 10.0012 | 15.0018 | 25.003 | 37.5045 | 50.006 | 95.552 | 97.123 | 97.41 | 97.362 | 97.005 | 96.688 | 96.195 | 97.446 | 97.741 | 97.833 | 97.604 | 97.357 | 97.062 | 98.074 | 98.229 | 98.119 | 97.965 | 97.765
SMA America | STP50-US-40 | PV Inverter | 500 | 725 | 800 | 480 | 50 | CEC Inverter Database | 480V | SMA-America-STP50-US-40-480V | Y | 5.1 | 5.0072 | 10.0144 | 15.0216 | 25.036 | 37.554 | 50.072 | 94.9771 | 97.1941 | 97.7158 | 97.8318 | 97.5793 | 97.2902 | 96.4618 | 97.7508 | 98.1301 | 98.2175 | 98.0757 | 97.8645 | 97.214 | 97.859 | 98.0248 | 97.7868 | 98.1846 | 97.8628
SMA America | STP 62-US-41 | PV Inverter | 500 | 725 | 800 | 480 | 62.5 | CEC Inverter Database | 480V | SMA-America-STP-62-US-41-480V | Y | 5.43 | 6.25 | 12.5 | 18.75 | 31.25 | 46.875 | 62.5 | 96.186 | 97.249 | 97.41 | 97.376 | 97.171 | 96.538 | 96.699 | 97.65 | 97.804 | 97.788 | 97.42 | 97.048 | 97.377 | 98.172 | 98.225 | 98.063 | 97.819 | 97.457
SMA America | SHP 125-US-20 | PV Inverter | 705 | 830 | 1200 | 480 | 125 | CEC Inverter Database | 480V | SMA-America-SHP-125-US-20-480V | Y | 5.37 | 12.5007 | 25.0014 | 37.5021 | 62.5035 | 93.7553 | 125.007 | 98.7556 | 98.9976 | 98.8838 | 98.8276 | 98.6062 | 98.2844 | 98.4402 | 98.8236 | 98.6952 | 98.6274 | 98.4048 | 98.0538 | 97.4702 | 98.0424 | 98.235 | 98.2842 | 98.1476 | 97.8116
SMA America | SHP 150-US-20 | PV Inverter | 880 | 960 | 1200 | 600 | 150 | CEC Inverter Database | 600V | SMA-America-SHP-150-US-20-600V | Y | 6.63 | 15.0079 | 30.0157 | 45.0236 | 75.0393 | 112.559 | 150.0787 | 98.7136 | 99.052 | 98.979 | 98.955 | 98.8152 | 98.582 | 98.722 | 99.0322 | 99.0162 | 98.9622 | 98.7618 | 98.5232 | 98.0838 | 98.6294 | 98.704 | 98.7056 | 98.5702 | 98.3194
SMA America | SC-1850-US | PV Inverter | 570 | 665 | 950 | 385 | 1661 | CEC Inverter Database | 385V | SMA-America-SC-1850-US-385V | Y | 294 | 166.1 | 332.2 | 498.3 | 830.5 | 1245.75 | 1661 | 96.09 | 97.54 | 97.81 | 97.79 | 97.59 | 97.25 | 95.5 | 97.22 | 97.55 | 97.62 | 97.45 | 97.13 | 93.24 | 96.22 | 96.74 | 97.07 | 96.98 | 96.67
SMA America | SC-2200-US | PV Inverter | 570 | 665 | 950 | 385 | 2079 | CEC Inverter Database | 385V | SMA-America-SC-2200-US-385V | Y | 297 | 207.9 | 415.8 | 623.7 | 1039.5 | 1559.25 | 2079 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18
SMA America | SC 2500-EV-US | PV Inverter | 850 | 994 | 1425 | 550 | 2353.87 | CEC Inverter Database | 550V | SMA-America-SC-2500-EV-US-550V | Y | 370 | 235.39 | 470.77 | 706.16 | 1176.94 | 1765.4 | 2353.87 | 96.42 | 97.63 | 97.83 | 97.79 | 97.42 | 96.82 | 95.86 | 97.35 | 97.63 | 97.65 | 97.28 | 96.74 | 94.25 | 96.58 | 97.07 | 97.2 | 96.81 | 96.42
SMA America | SC 2750-EV-US | PV Inverter | 875 | 957 | 1200 | 600 | 2600 | CEC Inverter Database | 600V | SMA-America-SC-2750-EV-US-600V | Y | 379.32 | 260 | 520 | 780 | 1300 | 1950 | 2600 | 95.6543 | 97.2785 | 97.676 | 97.8338 | 97.6424 | 97.2188 | 95.3931 | 97.1422 | 97.5611 | 97.7454 | 97.5481 | 97.0711 | 94.4709 | 96.7352 | 97.0588 | 97.4894 | 97.3596 | 96.8887
SMA America | SC 4000 UP-US 600V 3850A | PV Inverter | 880 | 970 | 1200 | 600 | 3650.134 | CEC Inverter Database | 600V | SMA-America-SC-4000-UP-US-600V-3850A-600V | Y | 453.5 | 365.0134 | 730.0268 | 1095.0402 | 1825.067 | 2737.6005 | 3650.134 | 98.2807 | 98.7001 | 98.7205 | 98.6249 | 98.4911 | 98.1606 | 98.0525 | 98.5891 | 98.6273 | 98.5552 | 98.3953 | 98.0229 | 97.3227 | 98.2881 | 98.4129 | 98.4176 | 98.2202 | 97.8437
SMA America | SC 4200 UP-US 630V 3850A | PV Inverter | 921 | 1001 | 1200 | 630 | 3832.828 | CEC Inverter Database | 630V | SMA-America-SC-4200-UP-US-630V-3850A-630V | Y | 451.8 | 383.2828 | 766.5656 | 1149.8484 | 1916.414 | 2874.621 | 3832.828 | 98.2694 | 98.7021 | 98.6674 | 98.6466 | 98.5287 | 98.2119 | 97.9903 | 98.5997 | 98.6622 | 98.5939 | 98.4546 | 98.0872 | 97.504 | 98.3658 | 98.3947 | 98.4009 | 98.3081 | 97.9519
SMA America | SC 4400 UP-US 660V 3850A | PV Inverter | 962 | 1032 | 1200 | 660 | 4017.113 | CEC Inverter Database | 660V | SMA-America-SC-4400-UP-US-660V-3850A-660V | Y | 465.17 | 401.7113 | 803.4226 | 1205.1339 | 2008.5565 | 3012.8347 | 4017.113 | 98.287 | 98.7337 | 98.7105 | 98.7078 | 98.6023 | 98.295 | 98.1038 | 98.6371 | 98.6292 | 98.6406 | 98.5024 | 98.149 | 97.5982 | 98.4496 | 98.5884 | 98.4873 | 98.3886 | 98.0401
SMA America | SC 4600 UP-US 690V 3850A | PV Inverter | 1003 | 1062 | 1200 | 690 | 4198.235 | CEC Inverter Database | 690V | SMA-America-SC-4600-UP-US-690V-3850A-690V | Y | 471.07 | 419.8235 | 839.647 | 1259.4705 | 2099.1175 | 3148.6762 | 4198.235 | 98.2728 | 98.7421 | 98.7243 | 98.7352 | 98.6471 | 98.3477 | 98.1499 | 98.6747 | 98.6863 | 98.6911 | 98.5653 | 98.2147 | 97.7407 | 98.5298 | 98.644 | 98.5955 | 98.4551 | 98.1264
SolarEdge Technologies Ltd. | SE3000H-US | PV Inverter | 360 | 395 | 480 | 240 | 2.962 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3000H-US-240V | Y | 0 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17
SolarEdge Technologies Ltd. | SE3000x | PV Inverter | 100 | 388 | 480 | 240 | 3.01 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3000x-240V | Y | 3.39 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 95.1 | 97.1 | 97.5 | 97.8 | 97.8 | 97.7 | 94.8 | 96.8 | 97.4 | 97.7 | 97.7 | 97.6 | 93.4 | 96.4 | 97 | 97.4 | 97.5 | 97.5
SolarEdge Technologies Ltd. | SE3000x | PV Inverter | 305 | 350 | 480 | 208 | 3.02 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE3000x-208V | Y | 3.71 | 0.3 | 0.6 | 0.91 | 1.51 | 2.27 | 3.02 | 96 | 97.4 | 97.6 | 97.7 | 97.6 | 97.4 | 95.6 | 97.1 | 97.5 | 97.6 | 97.5 | 97.3 | 93.6 | 96.3 | 96.9 | 97.2 | 97.2 | 97.1
SolarEdge Technologies Ltd. | SE3300x | PV Inverter | 370 | 435 | 500 | 240 | 3.251 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3300x-240V | Y | 5.46 | 0.33 | 0.65 | 0.98 | 1.63 | 2.44 | 3.25 | 95.3 | 97.1 | 97.5 | 97.6 | 97.6 | 97.5 | 94.9 | 96.8 | 97.3 | 97.5 | 97.5 | 97.3 | 94.2 | 96.5 | 96.9 | 97.3 | 97.4 | 97.2
SolarEdge Technologies Ltd. | SE3800H-US | PV Inverter | 360 | 395 | 480 | 208 | 3.255 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE3800H-US-208V | Y | 4.12 | 0.3255 | 0.651 | 0.9765 | 1.6275 | 2.4413 | 3.255 | 89.795 | 99.3907 | 99.3812 | 99.2769 | 99.0026 | 98.7791 | 92.1061 | 99.3518 | 99.377 | 99.2454 | 98.986 | 98.7542 | 95.5802 | 99.4287 | 99.3924 | 99.2524 | 98.9976 | 98.7297
SolarEdge Technologies Ltd. | SE3300x | PV Inverter | 320 | 410 | 500 | 208 | 3.288 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE3300x-208V | Y | 5.55 | 0.33 | 0.66 | 0.99 | 1.64 | 2.47 | 3.29 | 95.5 | 97.2 | 97.3 | 97.4 | 97.2 | 97.4 | 94.8 | 96.7 | 97 | 97.2 | 97 | 96.8 | 93.5 | 96.3 | 96.6 | 96.9 | 96.9 | 96.8
SolarEdge Technologies Ltd. | SE3800H-US | PV Inverter | 360 | 395 | 480 | 240 | 3.747 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3800H-US-240V | Y | 0 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08
SolarEdge Technologies Ltd. | SE3800A-US | PV Inverter | 360 | 400 | 480 | 240 | 3.79 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3800A-US-240V | Y | 2.24 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8
SolarEdge Technologies Ltd. | SE3800A-US | PV Inverter | 320 | 410 | 500 | 208 | 3.99 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE3800A-US-208V | Y | 5.1 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4
SolarEdge Technologies Ltd. | SE5000H-US | PV Inverter | 360 | 395 | 480 | 208 | 4.979 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE5000H-US-208V | Y | 4.51 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.58 | 98.34 | 98.72 | 98.82 | 98.82 | 98.91 | 96.34 | 98.22 | 98.64 | 98.76 | 98.77 | 98.64 | 95.89 | 97.99 | 98.46 | 98.68 | 98.7 | 98.57
SolarEdge Technologies Ltd. | SE5000x | PV Inverter | 320 | 410 | 500 | 208 | 4.98 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE5000x-208V | Y | 5.46 | 0.5 | 1 | 1.49 | 2.49 | 3.73 | 4.98 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.6 | 95.9 | 97 | 97.2 | 97 | 97 | 96.6 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.5
SolarEdge Technologies Ltd. | SE5000x | PV Inverter | 370 | 400 | 480 | 240 | 4.99 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE5000x-240V | Y | 2.24 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 96.7 | 97.9 | 98.1 | 98.1 | 98.3 | 98.1 | 96.4 | 97.7 | 98 | 98 | 98.2 | 98 | 95.7 | 97.4 | 97.7 | 97.8 | 97.8 | 97.9
SolarEdge Technologies Ltd. | SE5000H-US | PV Inverter | 360 | 395 | 480 | 240 | 5.052 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE5000H-US-240V | Y | 4.52 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.65 | 98.42 | 98.79 | 99 | 98.97 | 99.11 | 96.38 | 98.28 | 98.7 | 98.94 | 98.92 | 98.86 | 96.03 | 98.07 | 98.57 | 98.87 | 98.87 | 98.81
SolarEdge Technologies Ltd. | SE6000H-US | PV Inverter | 360 | 395 | 480 | 208 | 5.054 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE6000H-US-208V | Y | 4.52 | 0.5054 | 1.0108 | 1.5162 | 2.527 | 3.7905 | 5.054 | 96.6546 | 98.421 | 98.7873 | 99.0003 | 98.9676 | 99.1108 | 96.3757 | 98.2834 | 98.7004 | 98.9384 | 98.9206 | 98.8604 | 96.0285 | 98.0689 | 98.5658 | 98.8689 | 98.8702 | 98.8054
SolarEdge Technologies Ltd. | SE6000x | PV Inverter | 320 | 410 | 500 | 208 | 5.33 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE6000x-208V | Y | 5.22 | 0.53 | 1.07 | 1.6 | 2.66 | 3.99 | 5.33 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.4 | 95.9 | 97 | 97.2 | 97 | 97 | 96.4 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.3
SolarEdge Technologies Ltd. | SE6000x | PV Inverter | 370 | 435 | 500 | 240 | 5.99 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE6000x-240V | Y | 3.52 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 5.99 | 96.5 | 97.6 | 97.7 | 97.5 | 97.3 | 97 | 96 | 97.4 | 97.5 | 97.3 | 97.3 | 97 | 95.7 | 97.1 | 97.3 | 97.2 | 97.3 | 96.9
SolarEdge Technologies Ltd. | SE6000H-US | PV Inverter | 360 | 395 | 480 | 240 | 6.046 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE6000H-US-240V | Y | 4.52 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71
SolarEdge Technologies Ltd. | SE7600A-US | PV Inverter | 325 | 375 | 480 | 208 | 7.56 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE7600A-US-208V | Y | 5.75 | 0.756 | 1.512 | 2.268 | 3.78 | 5.67 | 7.56 | 96.3 | 97.4 | 97.6 | 97.6 | 97.5 | 97.3 | 96 | 97.2 | 97.5 | 97.5 | 97.4 | 97.2 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.8
SolarEdge Technologies Ltd. | SE7600H-US | PV Inverter | 360 | 395 | 480 | 240 | 7.616 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE7600H-US-240V | Y | 4.52 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71
SolarEdge Technologies Ltd. | SE7600A-US | PV Inverter | 360 | 400 | 480 | 240 | 7.625 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE7600A-US-240V | Y | 2.16 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1
SolarEdge Technologies Ltd. | SE9KUS | PV Inverter | 384 | 424 | 504 | 208 | 8.963 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE9KUS-208V | Y | 3.08 | 0.9 | 1.79 | 2.69 | 4.48 | 6.72 | 8.96 | 95.2 | 96.5 | 96.8 | 96.6 | 96.3 | 96.1 | 94.9 | 96.3 | 96.7 | 96.5 | 96.3 | 96 | 94.3 | 96 | 96.4 | 96.4 | 96.1 | 95.8
SolarEdge Technologies Ltd. | SE10KUS | PV Inverter | 100 | 882 | 962 | 480 | 9.85 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE10KUS-480V | Y | 3.13 | 0.98 | 1.97 | 2.95 | 4.92 | 7.38 | 9.85 | 95.5 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 95.1 | 97.3 | 97.7 | 98 | 98 | 97.9 | 94.2 | 97 | 97.5 | 97.9 | 98 | 97.9
SolarEdge Technologies Ltd. | SE10000A-US | PV Inverter | 325 | 375 | 480 | 208 | 9.93 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE10000A-US-208V | Y | 5.75 | 0.993 | 1.986 | 2.979 | 4.965 | 7.448 | 9.93 | 96.8 | 97.6 | 97.7 | 97.5 | 97.4 | 97.1 | 96.5 | 97.4 | 97.5 | 97.4 | 97.2 | 96.9 | 96.2 | 97 | 97.2 | 97.1 | 96.9 | 96.7
SolarEdge Technologies Ltd. | SE10000A-US | PV Inverter | 360 | 400 | 480 | 240 | 9.94 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE10000A-US-240V | Y | 5.95 | 0.99 | 1.99 | 2.98 | 4.97 | 7.46 | 9.94 | 96.8 | 97.6 | 97.8 | 97.8 | 97.7 | 97.5 | 96.6 | 97.5 | 97.7 | 97.6 | 97.6 | 97.4 | 96.4 | 97.3 | 97.5 | 97.4 | 97.4 | 97.2
SolarEdge Technologies Ltd. | SE10000H-US | PV Inverter | 360 | 395 | 480 | 240 | 9.994 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE10000H-US-240V | Y | 6 | 0.999 | 1.999 | 2.998 | 4.997 | 7.496 | 9.994 | 97.86 | 98.83 | 98.94 | 99.23 | 98.95 | 98.63 | 97.69 | 98.74 | 98.88 | 99.18 | 98.91 | 98.55 | 97.44 | 98.54 | 98.68 | 98.7 | 98.62 | 98.1
SolarEdge Technologies Ltd. | SE11400H-US | PV Inverter | 360 | 395 | 480 | 208 | 10.001 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE11400H-US-208V | Y | 5.71 | 1.0001 | 2.0001 | 3.0002 | 5.0003 | 7.5004 | 10.0006 | 97.7682 | 98.7285 | 98.8322 | 99.0698 | 98.6681 | 98.1747 | 97.6539 | 98.6608 | 98.771 | 98.9695 | 98.5754 | 98.0908 | 97.439 | 98.5357 | 98.6979 | 98.696 | 98.62 | 98.0972
SolarEdge Technologies Ltd. | SE11400A-US | PV Inverter | 360 | 400 | 480 | 240 | 11.39 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE11400A-US-240V | Y | 5.95 | 1.139 | 2.278 | 3.417 | 5.695 | 8.543 | 11.39 | 96.9 | 97.7 | 97.8 | 97.8 | 97.6 | 97.4 | 96.8 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 96.5 | 97.4 | 97.5 | 97.5 | 97.3 | 97.1
SolarEdge Technologies Ltd. | SE11400H-US | PV Inverter | 360 | 395 | 480 | 240 | 11.393 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE11400H-US-240V | Y | 6 | 1.139 | 2.279 | 3.418 | 5.697 | 8.545 | 11.393 | 97.88 | 98.84 | 98.95 | 99.16 | 98.82 | 98.41 | 97.91 | 98.83 | 98.93 | 99.17 | 98.83 | 98.4 | 97.42 | 98.63 | 98.79 | 98.82 | 98.8 | 98.39
SolarEdge Technologies Ltd. | SE14.4KUS | PV Inverter | 400 | 460 | 600 | 208 | 14.51 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE14.4KUS-208V | Y | 4.16 | 1.45 | 2.9 | 4.35 | 7.26 | 10.88 | 14.51 | 95.9 | 97.3 | 97.5 | 97.5 | 97 | 96.6 | 95.2 | 97.1 | 97.2 | 97.3 | 97.2 | 96.8 | 94.7 | 96.3 | 96.7 | 96.9 | 96.4 | 96.2
SolarEdge Technologies Ltd. | SE43.2KUS | PV Inverter | 400 | 460 | 600 | 208 | 14.51 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE43.2KUS-208V | Y | 4.16 | 1.451 | 2.902 | 4.353 | 7.255 | 10.8825 | 14.51 | 95.8927 | 97.2782 | 97.4837 | 97.462 | 97.0093 | 96.6434 | 95.2252 | 97.0865 | 97.1922 | 97.3046 | 97.1963 | 96.8019 | 94.6669 | 96.2868 | 96.6724 | 96.8566 | 96.3889 | 96.1759
SolarEdge Technologies Ltd. | SE17.3KUS | PV Inverter | 400 | 460 | 600 | 208 | 16.564 | CEC Inverter Database | 208V | SolarEdge-Technologies-Ltd.-SE17.3KUS-208V | Y | 5.28 | 1.6564 | 3.3128 | 4.9691 | 8.2819 | 12.4228 | 16.5638 | 96.254 | 97.276 | 97.532 | 97.31 | 96.986 | 96.694 | 95.77 | 97.01 | 97.108 | 97.13 | 96.79 | 96.474 | 94.76 | 96.44 | 96.656 | 96.86 | 96.53 | 96.138
SolarEdge Technologies Ltd. | SE20KUS | PV Inverter | 842 | 882 | 962 | 480 | 20.05 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE20KUS-480V | Y | 3.48 | 2.01 | 4.01 | 6.02 | 10.03 | 15.04 | 20.05 | 96.6 | 97.6 | 97.9 | 98 | 98 | 97.9 | 96.6 | 97.5 | 97.9 | 98 | 98 | 97.9 | 96 | 97.3 | 97.7 | 97.9 | 97.8 | 97.8
SolarEdge Technologies Ltd. | SE30KUS | PV Inverter | 790 | 850 | 950 | 480 | 30.159 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE30KUS-480V | Y | 7.06 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.4085 | 98.3647 | 98.5506 | 98.5075 | 98.4804 | 98.3856 | 97.0794 | 98.2049 | 98.429 | 98.4194 | 98.4029 | 98.314 | 96.4164 | 97.9007 | 98.2089 | 98.2953 | 98.2622 | 98.2
SolarEdge Technologies Ltd. | SE100KUS | PV Inverter | 790 | 850 | 950 | 480 | 33.3 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE100KUS-480V | Y | 5.05 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595
SolarEdge Technologies Ltd. | SE33.3KUS | PV Inverter | 790 | 850 | 950 | 480 | 33.3 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE33.3KUS-480V | Y | 5.05 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.2 | 98.2 | 98.9 | 98.5 | 98.7 | 98.5 | 96.7 | 98.1 | 98.1 | 98.5 | 98.4 | 98.2 | 96.3 | 97.8 | 97.8 | 98.5 | 98.3 | 98.2
SolarEdge Technologies Ltd. | SE66.6KUS | PV Inverter | 790 | 850 | 950 | 480 | 33.3 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE66.6KUS-480V | Y | 5.05 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595
SolarEdge Technologies Ltd. | SE120KUS | PV Inverter | 790 | 850 | 950 | 480 | 40.252 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE120KUS-480V | Y | 7.43 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994
SolarEdge Technologies Ltd. | SE40KUS | PV Inverter | 790 | 850 | 950 | 480 | 40.252 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE40KUS-480V | Y | 7.43 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994
SolarEdge Technologies Ltd. | SE80KUS | PV Inverter | 790 | 850 | 950 | 480 | 40.252 | CEC Inverter Database | 480V | SolarEdge-Technologies-Ltd.-SE80KUS-480V | Y | 7.43 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994
Solaria Corporation | Solaria PowerXT-345R-AC | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-345R-AC-240V | Y | 0.025 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1
Solaria Corporation | Solaria PowerXT-350R-AC | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-350R-AC-240V | Y | 0.025 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1
Solaria Corporation | Solaria PowerXT-355R-AC | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-355R-AC-240V | Y | 0.025 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1
Solaria Corporation | Solaria PowerXT-360R-AC | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-360R-AC-240V | Y | 0.025 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1
Solaria Corporation | Solaria PowerXT-365R-AC | PV Inverter | 27 | 36 | 45 | 240 | 0.29 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-365R-AC-240V | Y | 0.025 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757
Solaria Corporation | Solaria PowerXT-395R-PM-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-395R-PM-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Solaria Corporation | Solaria PowerXT-400R-PM-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-400R-PM-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Solaria Corporation | Solaria PowerXT-410R-PM-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-410R-PM-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
Solaria Corporation | Solaria PowerXT-420R-PM-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.3487 | CEC Inverter Database | 240V | Solaria-Corporation-Solaria-PowerXT-420R-PM-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SolarJuice American Inc. | S4A-H60 | PV Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H60-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
SolarJuice American Inc. | S4A-H70 | PV Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H70-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
SolarJuice American Inc. | S4A-H76 | PV Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H76-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
SolarJuice American Inc. | S4A-H86 | PV Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H86-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
Sol-Ark | Sol-Ark-8k-48-ST | PV Inverter | 240 | 370 | 425 | 208 | 7.839 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-8k-48-ST-208V | Y | 13.4 | 0.78393 | 1.5679 | 2.3518 | 3.9196 | 5.8795 | 7.8393 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631
Sol-Ark | Sol-Ark-8k-48-ST | PV Inverter | 240 | 370 | 425 | 240 | 7.976 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-8k-48-ST-240V | Y | 13.4 | 0.79762 | 1.5952 | 2.3928 | 3.9881 | 5.9821 | 7.9762 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868
Sol-Ark | Sol-Ark-12K-P | PV Inverter | 240 | 370 | 425 | 208 | 8.818 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-12K-P-208V | Y | 13.4 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098
Sol-Ark | Sol-Ark-9k-48-ST | PV Inverter | 240 | 370 | 425 | 208 | 8.818 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-9k-48-ST-208V | Y | 13.4 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098
Sol-Ark | Sol-Ark-12K-P | PV Inverter | 240 | 370 | 425 | 240 | 8.982 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-12K-P-240V | Y | 13.4 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494
Sol-Ark | Sol-Ark-9k-48-ST | PV Inverter | 240 | 370 | 425 | 240 | 8.982 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-9k-48-ST-240V | Y | 13.4 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-6.0-US | PV Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-6.0-US-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.0-US | PV Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-7.0-US-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.6-US | PV Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-7.6-US-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-8.6-US | PV Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-8.6-US-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
Sparq Systems | Q1200-4101 | PV Inverter | 28 | 29 | 31 | 240 | 1.165 | CEC Inverter Database | 240V | Sparq-Systems-Q1200-4101-240V | Y | 0.04 | 0.12 | 0.24 | 0.36 | 0.6 | 0.9 | 1.2 | 91.2693 | 95.4412 | 96.5736 | 97.1364 | 97.0548 | 96.7999 | 90.983 | 95.514 | 96.5823 | 97.0419 | 96.9805 | 96.7573 | 89.75 | 95.2351 | 96.4213 | 97.0117 | 96.9939 | 96.8163
Sparq Systems | Q1200-4102 | PV Inverter | 36 | 37 | 38 | 240 | 1.203 | CEC Inverter Database | 240V | Sparq-Systems-Q1200-4102-240V | Y | 0.04 | 0.12032 | 0.24064 | 0.36096 | 0.6016 | 0.9024 | 1.2032 | 88.21 | 94.58 | 96.05 | 97.188 | 97.44 | 97.345 | 87.2763 | 94.772 | 96.19 | 97.21 | 97.36 | 97.235 | 87.1383 | 95.037 | 96.348 | 97.161 | 97.327 | 97.225
Sungrow Power Supply Co., Ltd. | SG36CX-US | PV Inverter | 550 | 710 | 850 | 480 | 36.046 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SG36CX-US-480V | Y | 3.7 | 3.6046 | 7.2093 | 10.8139 | 18.0232 | 27.0347 | 36.0463 | 96.1175 | 97.2055 | 97.5335 | 97.7479 | 97.742 | 97.5065 | 97.1732 | 98.2799 | 98.5254 | 98.5967 | 98.521 | 98.2451 | 96.4094 | 97.7387 | 98.065 | 98.2558 | 98.2296 | 98.1549
Sungrow Power Supply Co., Ltd. | SG60KU-M | PV Inverter | 550 | 700 | 850 | 480 | 60 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SG60KU-M-480V | Y | 0.88 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.2 | 98.2 | 98.4 | 98.4 | 98 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 97.5 | 98.6 | 98.5 | 98.8 | 98.5 | 98.4
Sungrow Power Supply Co., Ltd. | SG60CX-US | PV Inverter | 550 | 710 | 850 | 480 | 60.182 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SG60CX-US-480V | Y | 3.38 | 6.0182 | 12.0363 | 18.0545 | 30.0908 | 45.1361 | 60.1815 | 96.9202 | 97.6109 | 97.7932 | 97.9095 | 97.8059 | 97.5258 | 98.1961 | 98.7137 | 98.8428 | 98.8099 | 98.6523 | 98.2665 | 97.4526 | 98.1491 | 98.2803 | 98.3385 | 98.2104 | 98.0212
Sungrow Power Supply Co., Ltd. | SG125HV | PV Inverter | 860 | 945 | 1200 | 600 | 125 | CEC Inverter Database | 600V | Sungrow-Power-Supply-Co.,-Ltd.-SG125HV-600V | Y | 5.59 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5862 | 98.8265 | 98.8829 | 98.6821 | 98.4462 | 98.2555 | 98.2896 | 98.5839 | 98.589 | 98.4937 | 98.3596 | 98.1057 | 98.0848 | 98.4261 | 98.4778 | 98.3839 | 98.0971 | 97.6269
Sungrow Power Supply Co., Ltd. | SG250HX-US | PV Inverter | 860 | 1080 | 1300 | 800 | 226.997 | CEC Inverter Database | 800V | Sungrow-Power-Supply-Co.,-Ltd.-SG250HX-US-800V | Y | 5.21 | 22.6997 | 45.3994 | 68.0992 | 113.4986 | 170.2479 | 226.9972 | 97.0577 | 98.2506 | 98.469 | 98.5708 | 98.4621 | 98.262 | 98.195 | 98.7627 | 98.9461 | 99.0101 | 98.869 | 98.6779 | 97.9983 | 98.6612 | 98.8997 | 98.9478 | 98.8178 | 98.632
Sungrow Power Supply Co., Ltd. | SC1000KU | PV Inverter | 810 | 1005 | 1200 | 540 | 1001.306 | CEC Inverter Database | 540V | Sungrow-Power-Supply-Co.,-Ltd.-SC1000KU-540V | Y | 83.7646 | 100.1306 | 200.2612 | 300.3918 | 500.653 | 750.9795 | 1001.306 | 94.9956 | 96.8144 | 97.2437 | 97.3155 | 97.0286 | 96.6633 | 94.2811 | 96.3444 | 96.9047 | 97.0479 | 96.8017 | 96.439 | 93.6894 | 95.9275 | 96.5802 | 96.8324 | 96.5978 | 96.1882
Sungrow Power Supply Co., Ltd. | SG2500U | PV Inverter | 800 | 900 | 1200 | 550 | 2500 | CEC Inverter Database | 550V | Sungrow-Power-Supply-Co.,-Ltd.-SG2500U-550V | Y | 651.36 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 98 | 98.6 | 98.8 | 98.8 | 98.6 | 98.4 | 97.8 | 98.5 | 98.6 | 98.6 | 98.5 | 98.3 | 97.4 | 98.2 | 98.4 | 98.5 | 98.3 | 98.2
SunPower | SPR-E19-320-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-E19-320-BLK-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-E19-320-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-E19-320-BLK-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-E19-320-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-E19-320-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-E19-320-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-E19-320-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-E20-325-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-E20-325-BLK-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-E20-325-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-E20-325-BLK-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-E20-327-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-E20-327-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-E20-327-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-E20-327-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-E20-335-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-E20-335-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-E20-335-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-E20-335-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X20-327-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X20-327-BLK-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X20-327-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X20-327-BLK-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X20-327-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X20-327-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X20-327-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X20-327-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X21-335-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X21-335-BLK-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X21-335-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X21-335-BLK-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X21-335-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X21-335-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X21-335-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X21-335-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X21-345-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X21-345-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X21-345-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X21-345-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X21-350-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X21-350-BLK-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X21-350-BLK-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X21-350-BLK-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X22-360-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X22-360-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X22-360-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X22-360-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | SPR-X22-370-E-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.315 | CEC Inverter Database | 208V | SunPower-SPR-X22-370-E-AC-208V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197
SunPower | SPR-X22-370-E-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.315 | CEC Inverter Database | 240V | SunPower-SPR-X22-370-E-AC-240V | Y | 0.021 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825
SunPower | MI-C-320-US208/240-1X | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-MI-C-320-US208-240-1X-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | MI-C-320-US208/240-1X | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-MI-C-320-US208-240-1X-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-E19-320-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-E19-320-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-E19-320-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-E19-320-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-E20-327-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-E20-327-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-E20-327-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-E20-327-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X20-327-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X20-327-BLK-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X20-327-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X20-327-BLK-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X20-327-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X20-327-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X20-327-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X20-327-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X21-335-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X21-335-BLK-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X21-335-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X21-335-BLK-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X21-335-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X21-335-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X21-335-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X21-335-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X21-345-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X21-345-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X21-345-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X21-345-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X21-350-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X21-350-BLK-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X21-350-BLK-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X21-350-BLK-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X22-360-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X22-360-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X22-360-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X22-360-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-X22-370-D-AC | PV Inverter | 53 | 60 | 64 | 208 | 0.32 | CEC Inverter Database | 208V | SunPower-SPR-X22-370-D-AC-208V | Y | 0.02 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9
SunPower | SPR-X22-370-D-AC | PV Inverter | 53 | 60 | 64 | 240 | 0.32 | CEC Inverter Database | 240V | SunPower-SPR-X22-370-D-AC-240V | Y | 0.1 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2
SunPower | SPR-A380-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A380-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A385-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A385-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A390-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A390-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A390-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A390-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A395-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A395-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A395-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A395-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A400-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A400-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A400-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A400-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A405-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A405-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A405-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A405-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A410-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A410-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A410-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A410-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A415-BLK-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A415-BLK-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A415-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A415-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A420-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A420-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A425-G-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.349 | CEC Inverter Database | 240V | SunPower-SPR-A425-G-AC-240V | Y | 0.019 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604
SunPower | SPR-A380-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A380-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A385-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A385-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A390-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A390-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A390-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A390-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A395-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A395-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A395-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A395-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A400-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A400-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A400-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A400-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A405-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A405-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A405-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A405-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A410-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A410-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A410-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A410-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A415-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A415-BLK-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A415-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A415-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A420-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A420-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A425-H-AC | PV Inverter | 38 | 40.5 | 43 | 208 | 0.367 | CEC Inverter Database | 208V | SunPower-SPR-A425-H-AC-208V | Y | 0.05 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185
SunPower | SPR-A380-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A380-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A385-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A385-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A390-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A390-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A390-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A390-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A395-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A395-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A395-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A395-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A400-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A400-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A400-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A400-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A405-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A405-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A405-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A405-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A410-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A410-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A410-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A410-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A415-BLK-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A415-BLK-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A415-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A415-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A420-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A420-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-A425-H-AC | PV Inverter | 38 | 40.5 | 43 | 240 | 0.384 | CEC Inverter Database | 240V | SunPower-SPR-A425-H-AC-240V | Y | 0.06 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854
SunPower | SPR-12000m-3 | PV Inverter | 300 | 675 | 800 | 480 | 12 | CEC Inverter Database | 480V | SunPower-SPR-12000m-3-480V | Y | 1.79 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898
SunPower | SPR-12000m-3-H | PV Inverter | 300 | 675 | 800 | 480 | 12 | CEC Inverter Database | 480V | SunPower-SPR-12000m-3-H-480V | Y | 1.79 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898
SunPower | SPR-15000m-3 | PV Inverter | 300 | 675 | 800 | 480 | 15 | CEC Inverter Database | 480V | SunPower-SPR-15000m-3-480V | Y | 1.79 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572
SunPower | SPR-15000m-3-H | PV Inverter | 300 | 675 | 800 | 480 | 15 | CEC Inverter Database | 480V | SunPower-SPR-15000m-3-H-480V | Y | 1.79 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572
SunPower | SPR-20000m-3 | PV Inverter | 380 | 695 | 800 | 480 | 20 | CEC Inverter Database | 480V | SunPower-SPR-20000m-3-480V | Y | 1.79 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422
SunPower | SPR-20000m-3-H | PV Inverter | 380 | 695 | 800 | 480 | 20 | CEC Inverter Database | 480V | SunPower-SPR-20000m-3-H-480V | Y | 1.79 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422
SunPower | SPR-24000m-3 | PV Inverter | 450 | 712 | 800 | 480 | 24.06 | CEC Inverter Database | 480V | SunPower-SPR-24000m-3-480V | Y | 1.79 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823
SunPower | SPR-24000m-3-H | PV Inverter | 450 | 712 | 800 | 480 | 24.06 | CEC Inverter Database | 480V | SunPower-SPR-24000m-3-H-480V | Y | 1.79 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823
SunPower | SPR-30000m-3 | PV Inverter | 500 | 720 | 800 | 480 | 30.01 | CEC Inverter Database | 480V | SunPower-SPR-30000m-3-480V | Y | 1.22 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08
Tabuchi Electric Co., Ltd. | THD-S55P3BB-US | PV Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THD-S55P3BB-US-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9
Tabuchi Electric Co., Ltd. | THD-S55P3B-US | PV Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THD-S55P3B-US-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9
Tabuchi Electric Co., Ltd. | THE-S55P3BB-USW | PV Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THE-S55P3BB-USW-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.326 | 93.286 | 94.304 | 94.656 | 94.048 | 94.174 | 89.688 | 93.666 | 94.706 | 95.44 | 95.498 | 95.41 | 88.78 | 93.076 | 94.276 | 95.094 | 95.166 | 94.922
Tesla Inc. | 1534000-xx-y | PV Inverter | 270 | 375 | 480 | 208 | 3.336 | CEC Inverter Database | 208V | Tesla-Inc.-1534000-xx-y-208V | Y | 3.8925 | 0.33357 | 0.66713 | 1.0007 | 1.6678 | 2.5017 | 3.3357 | 94.5015 | 95.4052 | 96.9255 | 97.3899 | 97.339 | 97.0429 | 97.5109 | 95.4805 | 97.2538 | 96.8148 | 97.9621 | 97.4384 | 95.4081 | 96.0018 | 96.4123 | 97.3319 | 97.8399 | 97.5201
Tesla Inc. | 1534000-xx-y | PV Inverter | 270 | 350 | 425 | 240 | 3.8 | CEC Inverter Database | 240V | Tesla-Inc.-1534000-xx-y-240V | Y | 4.664 | 0.38004 | 0.76008 | 1.1401 | 1.9002 | 2.8503 | 3.8004 | 93.3952 | 96.6818 | 96.8269 | 97.6523 | 97.789 | 97.1339 | 94.0344 | 97.5046 | 97.6631 | 98.024 | 98.074 | 97.6865 | 92.4631 | 96.097 | 97.7065 | 98.1107 | 98.0548 | 97.938
Tesla Inc. | 1538000-xx-y | PV Inverter | 270 | 375 | 480 | 208 | 6.561 | CEC Inverter Database | 208V | Tesla-Inc.-1538000-xx-y-208V | Y | 6.7176 | 0.65614 | 1.3123 | 1.9684 | 3.2807 | 4.9211 | 6.5614 | 93.438 | 98.4475 | 97.3037 | 97.8393 | 97.6255 | 96.8692 | 95.0991 | 98.0957 | 98.0608 | 98.1575 | 97.8955 | 98.2213 | 95.1054 | 96.6131 | 96.4097 | 97.8988 | 97.5475 | 97.0402
Tesla Inc. | 1538000-xx-y | PV Inverter | 270 | 375 | 480 | 240 | 7.575 | CEC Inverter Database | 240V | Tesla-Inc.-1538000-xx-y-240V | Y | 6.913 | 0.75749 | 1.515 | 2.2725 | 3.7875 | 5.6812 | 7.5749 | 93.5744 | 97.8119 | 98.3803 | 98.2034 | 97.8671 | 97.2554 | 96.846 | 97.8731 | 98.2225 | 98.5652 | 98.2426 | 97.6983 | 95.9244 | 96.8399 | 98.117 | 98.3572 | 98.0899 | 97.6444
TMEIC | PVU-L0840GR | PV Inverter | 915 | 1150 | 1200 | 630 | 794.693 | CEC Inverter Database | 630V | TMEIC-PVU-L0840GR-630V | Y | 47.17 | 79.469 | 158.939 | 23.8407 | 397.346 | 596.02 | 794.693 | 93.5562 | 97.2253 | 97.9043 | 98.4527 | 98.639 | 98.7216 | 93.0512 | 96.7995 | 97.5749 | 98.1032 | 98.3158 | 98.2723 | 92.8149 | 96.6179 | 97.4354 | 98.0106 | 98.2316 | 98.2048
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB6000SHU | PV Inverter | 200 | 380 | 460 | 208 | 4.992 | CEC Inverter Database | 208V | Trina-Energy-Storage-Solutions-(Jiangsu)-Co.,-Ltd-TB6000SHU-208V | Y | 1.86 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 92.957 | 94.9487 | 95.9767 | 96.7593 | 96.8163 | 96.5806 | 95.5718 | 97.208 | 97.7454 | 97.945 | 97.7162 | 97.3118 | 94.612 | 96.6111 | 97.398 | 97.7397 | 97.624 | 97.2797
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB6000SHU | PV Inverter | 200 | 380 | 460 | 240 | 5.76 | CEC Inverter Database | 240V | Trina-Energy-Storage-Solutions-(Jiangsu)-Co.,-Ltd-TB6000SHU-240V | Y | 2.25 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.6482 | 95.423 | 96.4707 | 97.0891 | 97.0873 | 96.8107 | 96.1623 | 97.5847 | 98.0803 | 98.165 | 97.934 | 97.5803 | 95.2354 | 97.0478 | 97.7734 | 98.0001 | 97.8593 | 97.5051
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB8000SHU | PV Inverter | 270 | 380 | 460 | 208 | 6.656 | CEC Inverter Database | 208V | Trina-Energy-Storage-Solutions-(Jiangsu)-Co.,-Ltd-TB8000SHU-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 94.9781 | 96.8811 | 97.4182 | 97.6928 | 97.4986 | 97.1525
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB8000SHU | PV Inverter | 270 | 380 | 460 | 240 | 7.68 | CEC Inverter Database | 240V | Trina-Energy-Storage-Solutions-(Jiangsu)-Co.,-Ltd-TB8000SHU-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 95.6637 | 97.2768 | 97.7475 | 97.9312 | 97.7346 | 97.4232
TSUNESS Co., Ltd | TSOL-M1600P | PV Inverter | 36 | 42 | 48 | 240 | 1.551 | CEC Inverter Database | 240V | TSUNESS-Co.,-Ltd-TSOL-M1600P-240V | Y | 0.03 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591
WSTECH GmbH | APS800-PV-1-440-5 | PV Inverter | 648 | 1000 | 1500 | 440 | 814.167 | CEC Inverter Database | 440V | WSTECH-GmbH-APS800-PV-1-440-5-440V | Y | 91.4 | 81.4167 | 162.8334 | 244.2501 | 407.0835 | 610.6252 | 814.1669 | 96.8994 | 97.9207 | 98.1472 | 98.0855 | 97.7317 | 97.3005 | 97.156 | 97.9031 | 98.0845 | 97.9812 | 97.697 | 97.2751 | 96.5182 | 97.3518 | 97.6259 | 97.6679 | 97.3419 | 96.9571
WSTECH GmbH | APS870-PV-1-480-5 | PV Inverter | 770 | 1000 | 1470 | 480 | 872.029 | CEC Inverter Database | 480V | WSTECH-GmbH-APS870-PV-1-480-5-480V | Y | 91.402 | 87.2029 | 174.4058 | 261.6087 | 436.0145 | 654.0218 | 872.029 | 97.0815 | 98.1883 | 98.4162 | 98.4017 | 98.1322 | 97.7562 | 95.7664 | 97.2807 | 97.8339 | 98.0408 | 97.8593 | 97.5271 | 96.9374 | 97.6397 | 97.8465 | 97.7946 | 97.5592 | 97.1756
WSTECH GmbH | APS1600-PV-2-440-5 | PV Inverter | 648 | 1000 | 1500 | 440 | 1626.952 | CEC Inverter Database | 440V | WSTECH-GmbH-APS1600-PV-2-440-5-440V | Y | 91.4 | 162.6952 | 325.3904 | 488.0856 | 813.476 | 1220.214 | 1626.952 | 98.0396 | 98.5839 | 98.6684 | 98.5329 | 98.2151 | 97.8585 | 96.9836 | 97.9106 | 98.1157 | 98.1085 | 97.8527 | 97.453 | 96.318 | 97.3792 | 97.6608 | 97.7017 | 97.437 | 97.0028
WSTECH GmbH | APS1740-PV-2-480-5 | PV Inverter | 770 | 1000 | 1470 | 480 | 1735.36 | CEC Inverter Database | 480V | WSTECH-GmbH-APS1740-PV-2-480-5-480V | Y | 91.402 | 173.536 | 347.0721 | 520.6081 | 867.6802 | 1301.5204 | 1735.3605 | 96.2018 | 97.6354 | 98.0243 | 98.1239 | 97.9169 | 97.5975 | 95.6963 | 97.2746 | 97.7805 | 97.9519 | 97.7577 | 97.4332 | 94.3845 | 96.4707 | 97.0706 | 97.4161 | 97.3403 | 97.06
Xiamen Kehua Hengsheng Co., Ltd. | SPI50K-BHV | PV Inverter | 540 | 695 | 850 | 480 | 49.825 | CEC Inverter Database | 480V | Xiamen-Kehua-Hengsheng-Co.,-Ltd.-SPI50K-BHV-480V | Y | 2.8 | 4.983 | 9.966 | 14.949 | 24.915 | 37.3725 | 49.83 | 96.7703 | 96.973 | 97.3637 | 97.6805 | 97.7045 | 97.6785 | 97.3153 | 98.4954 | 98.6189 | 98.7698 | 98.6611 | 98.2836 | 96.5521 | 97.8957 | 98.1552 | 98.33 | 98.283 | 98.0881
Xiamen Kehua Hengsheng Co., Ltd. | SPI60K-BHV | PV Inverter | 540 | 695 | 850 | 480 | 59.668 | CEC Inverter Database | 480V | Xiamen-Kehua-Hengsheng-Co.,-Ltd.-SPI60K-BHV-480V | Y | 2.8 | 5.967 | 11.934 | 17.901 | 29.835 | 44.7525 | 59.67 | 97.0114 | 97.6315 | 97.6409 | 97.9122 | 97.5927 | 97.3714 | 98.5714 | 98.8538 | 98.8416 | 98.7205 | 98.6058 | 98.3476 | 97.7579 | 98.3751 | 98.523 | 98.3758 | 98.1648 | 97.9527
Yaskawa Solectria Solar | PVI20TL-480-R | PV Inverter | 560 | 735 | 850 | 480 | 20 | CEC Inverter Database | 480V | Yaskawa-Solectria-Solar-PVI20TL-480-R-480V | Y | 3 | 2.0112 | 4.0224 | 6.0336 | 10.056 | 15.0839 | 20.1119 | 96.9815 | 97.6652 | 97.8012 | 97.8313 | 97.6023 | 97.256 | 97.9016 | 98.3305 | 98.4819 | 98.4139 | 98.2956 | 98.149 | 97.5397 | 98.2151 | 98.3121 | 98.2684 | 98.1987 | 97.9889
Yaskawa Solectria Solar | PVI 25TL-208 | PV Inverter | 480 | 575 | 850 | 208 | 25 | CEC Inverter Database | 208V | Yaskawa-Solectria-Solar-PVI-25TL-208-208V | Y | 2.9 | 2.5432 | 5.0864 | 7.6296 | 12.716 | 19.074 | 25.432 | 95.687 | 96.8055 | 97.0311 | 97.0424 | 96.7769 | 96.4735 | 95.3071 | 96.2843 | 96.7871 | 96.7814 | 96.4829 | 96.1186 | 93.5943 | 95.6171 | 96.1229 | 96.3357 | 96.1514 | 95.85
Yaskawa Solectria Solar | PVI25TL-480-R | PV Inverter | 560 | 735 | 850 | 480 | 25 | CEC Inverter Database | 480V | Yaskawa-Solectria-Solar-PVI25TL-480-R-480V | Y | 3 | 2.5259 | 5.0517 | 7.5776 | 12.6294 | 18.944 | 25.2587 | 96.9119 | 97.6982 | 97.8295 | 97.8399 | 97.5971 | 97.2868 | 97.8973 | 98.3256 | 98.4773 | 98.4082 | 98.2817 | 98.0946 | 97.5003 | 98.1562 | 98.3137 | 98.2793 | 98.1854 | 97.9963
Yaskawa Solectria Solar | PVI 36TL-480 | PV Inverter | 540 | 730 | 800 | 480 | 36 | CEC Inverter Database | 480V | Yaskawa-Solectria-Solar-PVI-36TL-480-480V | Y | 0 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2
Yaskawa Solectria Solar | PVI 50TL-480 | PV Inverter | 480 | 730 | 850 | 480 | 50 | CEC Inverter Database | 480V | Yaskawa-Solectria-Solar-PVI-50TL-480-480V | Y | 0.88 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5
Yaskawa Solectria Solar | PVI 60TL-480 | PV Inverter | 540 | 730 | 850 | 480 | 60 | CEC Inverter Database | 480V | Yaskawa-Solectria-Solar-PVI-60TL-480-480V | Y | 0.88 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4
Yaskawa Solectria Solar | XGI 1500-125/125 | PV Inverter | 860 | 1050 | 1250 | 600 | 124.6176 | CEC Inverter Database | 600V | Yaskawa-Solectria-Solar-XGI-1500-125-125-600V | Y | 3.8421 | 12.4618 | 24.9235 | 37.3853 | 62.3088 | 93.4632 | 124.6176 | 98.4216 | 98.8698 | 98.9434 | 98.8944 | 98.8062 | 98.7204 | 97.0398 | 98.3964 | 98.442 | 98.5462 | 98.5064 | 98.4522 | 95.8522 | 97.5256 | 98.1534 | 98.2428 | 98.249 | 98.2622
Yaskawa Solectria Solar | XGI 1500-125/150 | PV Inverter | 860 | 1050 | 1250 | 600 | 124.6176 | CEC Inverter Database | 600V | Yaskawa-Solectria-Solar-XGI-1500-125-150-600V | Y | 3.8421 | 12.4618 | 24.9235 | 37.3853 | 62.3088 | 93.4632 | 124.6176 | 98.4216 | 98.8698 | 98.9434 | 98.8944 | 98.8062 | 98.7204 | 97.0398 | 98.3964 | 98.442 | 98.5462 | 98.5064 | 98.4522 | 95.8522 | 97.5256 | 98.1534 | 98.2428 | 98.249 | 98.2622
Yaskawa Solectria Solar | XGI 1500-150/166 | PV Inverter | 860 | 1100 | 1250 | 600 | 150 | CEC Inverter Database | 600V | Yaskawa-Solectria-Solar-XGI-1500-150-166-600V | Y | 2.75 | 15 | 30 | 45 | 75 | 112.5 | 150 | 98.4688 | 98.9332 | 98.9862 | 98.8872 | 98.8088 | 98.718 | 98.1948 | 98.2298 | 98.5054 | 98.5424 | 98.4976 | 98.38 | 98.2596 | 98.2596 | 98.2786 | 98.3684 | 98.298 | 98.178
Yaskawa Solectria Solar | XGI 1500-166/166 | PV Inverter | 860 | 1050 | 1250 | 600 | 165.1393 | CEC Inverter Database | 600V | Yaskawa-Solectria-Solar-XGI-1500-166-166-600V | Y | 3.8421 | 16.5139 | 33.0279 | 49.5418 | 82.5697 | 123.8545 | 165.1393 | 98.5516 | 99.0108 | 99.0266 | 98.8722 | 98.7684 | 98.6026 | 97.5988 | 98.6058 | 98.6698 | 98.5888 | 98.4886 | 98.3066 | 96.512 | 97.8936 | 98.1316 | 98.269 | 98.1834 | 98.0808
Yaskawa Solectria Solar | SGI 500XTM | PV Inverter | 545 | 615 | 820 | 380 | 507 | CEC Inverter Database | 380V | Yaskawa-Solectria-Solar-SGI-500XTM-380V | Y | 88.78 | 50.7 | 101.4 | 152.1 | 253.5 | 380.25 | 507 | 93.6 | 96.1 | 96.7 | 97.1 | 97.2 | 97.1 | 93.2 | 95.8 | 96.5 | 96.9 | 97 | 97 | 92.1 | 95.3 | 96.1 | 96.6 | 96.8 | 96.8
Yaskawa Solectria Solar | SGI 750XTM | PV Inverter | 545 | 615 | 820 | 380 | 753.2 | CEC Inverter Database | 380V | Yaskawa-Solectria-Solar-SGI-750XTM-380V | Y | 122.55 | 75.32 | 150.64 | 225.96 | 376.6 | 564.9 | 753.2 | 94 | 96.2 | 96.7 | 97 | 97 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 97 | 91.9 | 95.3 | 96.2 | 96.7 | 96.7 | 96.8
Note on G2: If rated voltage is a range, set to the voltage that corresponds to the characterization data.
Note on H2: For multi-output devices, this is the total power for all outputs
Note on L2: This column is set to "N" (no) for laboratory characterization device data sets that are largely redundant with another data set. Multiple instances of the same device under the same voltage conditions were eliminated, but multiple instances of the same device under different voltage conditions were retained.

## Battery Inverters
Device Metadata |  |  | Device Ratings |  |  |  |  | Characterization Metadata | Output Configuration |  |  | Efficiency Curve Data
Manufacturer | Model | Description | Minimum Voltage Input (V) | Rated Voltage Input (V) | Maximum Voltage Input (V) | Rated Voltage Output (V) | Rated Power Output (kW) | Efficiency Data Source | Disambiguation Suffix | Model Label | Use? | Night Tare Loss (W) | Power Level 10% (kW) | Power Level 20% (kW) | Power Level 30% (kW) | Power Level 50% (kW) | Power Level 75% (kW) | Power Level 100% (kW) | Efficiency @ Vmin 10% (%) | Efficiency @ Vmin 20% (%) | Efficiency @ Vmin 30% (%) | Efficiency @ Vmin 50% (%) | Efficiency @ Vmin 75% (%) | Efficiency @ Vmin 100% (%) | Efficiency @ Vnom 10% (%) | Efficiency @ Vnom 20% (%) | Efficiency @ Vnom 30% (%) | Efficiency @ Vnom 50% (%) | Efficiency @ Vnom 75% (%) | Efficiency @ Vnom 100% (%) | Efficiency @ Vmax 10% (%) | Efficiency @ Vmax 20% (%) | Efficiency @ Vmax 30% (%) | Efficiency @ Vmax 50% (%) | Efficiency @ Vmax 75% (%) | Efficiency @ Vmax 100% (%)
BYD Auto Industry Company Limited | BEG60KTL-U-R1 | Battery Inverter | 750 | 850 | 950 | 480 | 60.276 | CEC Inverter Database | 480V | BYD-Auto-Industry-Company-Limited-BEG60KTL-U-R1-480V | Y | 98 | 6.0276 | 12.0552 | 18.0828 | 30.138 | 45.207 | 60.276 | 92.2639 | 95.0925 | 95.9421 | 96.3742 | 96.2199 | 95.9526 | 91.6435 | 94.6529 | 95.5526 | 96.0407 | 95.9491 | 95.6573 | 91.2179 | 94.3735 | 95.3175 | 95.8259 | 95.7582 | 95.4622
BYD Auto Industry Company Limited | BEG500KTL-U | Battery Inverter | 780 | 890 | 1000 | 480 | 501.756 | CEC Inverter Database | 480V | BYD-Auto-Industry-Company-Limited-BEG500KTL-U-480V | Y | 2 | 50.1756 | 100.3512 | 150.5268 | 250.878 | 376.317 | 501.756 | 90.958 | 94.5322 | 95.7353 | 96.3971 | 96.4923 | 96.3587 | 90.5506 | 94.2426 | 95.3835 | 96.1757 | 96.2707 | 96.1176 | 89.9146 | 93.8477 | 95.0786 | 95.9497 | 96.0727 | 95.9028
BYD Auto Industry Company Limited | BEG500KTL-U/01 | Battery Inverter | 780 | 890 | 1000 | 480 | 501.756 | CEC Inverter Database | 480V | BYD-Auto-Industry-Company-Limited-BEG500KTL-U-01-480V | Y | 2 | 50.1756 | 100.3512 | 150.5268 | 250.878 | 376.317 | 501.756 | 90.958 | 94.5322 | 95.7353 | 96.3971 | 96.4923 | 96.3587 | 90.5506 | 94.2426 | 95.3835 | 96.1757 | 96.2707 | 96.1176 | 89.9146 | 93.8477 | 95.0786 | 95.9497 | 96.0727 | 95.9028
CE+T Energy Solutions Inc. | 30C | Battery Inverter | 550 | 700 | 850 | 480 | 29.99 | CEC Inverter Database | 480V | CE+T-Energy-Solutions-Inc.-30C-480V | Y | 56.8 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4
CE+T Energy Solutions Inc. | 30C3 | Battery Inverter | 550 | 700 | 850 | 480 | 29.99 | CEC Inverter Database | 480V | CE+T-Energy-Solutions-Inc.-30C3-480V | Y | 56.8 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4
Chint Power Systems America | CPS ECB30KTL-O/US | Battery Inverter | 450 | 660 | 800 | 480 | 30.26 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-ECB30KTL-O-US-480V | Y | 20 | 3.026 | 6.052 | 9.078 | 15.13 | 22.695 | 30.26 | 94.6505 | 96.0141 | 96.0641 | 96.6384 | 96.7254 | 96.6107 | 94.9588 | 96.6395 | 97.0651 | 97.2663 | 97.3067 | 97.205 | 96.0461 | 97.4821 | 97.7088 | 98.0111 | 97.9517 | 97.7971
Chint Power Systems America | CPS ECB62.5KTL-M/US-480 | Battery Inverter | 750 | 925 | 1100 | 480 | 62.552 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-ECB62.5KTL-M-US-480-480V | Y | 6.1 | 6.2552 | 12.5104 | 18.7656 | 31.276 | 46.914 | 62.552 | 97.3465 | 97.9921 | 98.095 | 98.1165 | 97.9762 | 97.7541 | 95.9685 | 97.3161 | 97.572 | 97.7175 | 97.6025 | 97.3576 | 94.5644 | 96.473 | 97.091 | 97.2707 | 97.195 | 96.9647
Chint Power Systems America | CPS ECB125KTL-M/US-480 | Battery Inverter | 750 | 925 | 1100 | 480 | 125.188 | CEC Inverter Database | 480V | Chint-Power-Systems-America-CPS-ECB125KTL-M-US-480-480V | Y | 5.8 | 12.5188 | 25.0376 | 37.5564 | 62.594 | 93.891 | 125.188 | 97.3827 | 97.8322 | 98.0844 | 98.0479 | 97.8368 | 97.5419 | 96.6968 | 97.3947 | 97.5562 | 97.6474 | 97.4809 | 97.1852 | 95.9715 | 96.9549 | 97.0383 | 97.264 | 97.1269 | 96.8405
Darfon Electronics Corp. | HB51xxxxxx | Battery Inverter | 48 | 53 | 56.5 | 240 | 4.665 | CEC Inverter Database | 240V | Darfon-Electronics-Corp.-HB51xxxxxx-240V | Y | 0.6021 | 0.46648 | 0.93296 | 1.3994 | 2.3324 | 3.4986 | 4.6648 | 82.1179 | 89.1571 | 90.2158 | 90.0063 | 88.7866 | 86.8904 | 82.0054 | 89.6871 | 91.1703 | 91.3826 | 90.5543 | 89.4695 | 80.8864 | 89.1741 | 90.9925 | 91.4401 | 91.1444 | 90.1807
Darfon Electronics Corp. | H5001xxxxxx | Battery Inverter | 300 | 360 | 380 | 240 | 4.844 | CEC Inverter Database | 240V | Darfon-Electronics-Corp.-H5001xxxxxx-240V | Y | 28.48 | 0.48442 | 0.96883 | 1.4533 | 2.4221 | 3.6331 | 4.8442 | 86.6736 | 92.8161 | 94.3502 | 95.2023 | 95.0579 | 94.4449 | 87.1365 | 93.1676 | 94.6479 | 95.4859 | 95.3797 | 94.8013 | 87.1729 | 93.1946 | 94.6523 | 95.4841 | 95.3494 | 94.7714
Darfon Electronics Corp. | H5000xxxxxx | Battery Inverter | 300 | 360 | 380 | 240 | 5.074 | CEC Inverter Database | 240V | Darfon-Electronics-Corp.-H5000xxxxxx-240V | Y | 0.43 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196
Delta Electronics | E4-TL-US | Battery Inverter | 200 | 380 | 480 | 208 | 3.36 | CEC Inverter Database | 208V | Delta-Electronics-E4-TL-US-208V | Y | 1.21 | 0.33599 | 0.67197 | 1.008 | 1.6799 | 2.5199 | 3.3599 | 92.7058 | 95.316 | 96.0794 | 96.9375 | 97.261 | 97.2579 | 94.6716 | 96.7433 | 97.431 | 97.8832 | 97.9342 | 97.8306 | 93.5334 | 96.0786 | 96.9192 | 97.5645 | 97.7603 | 97.6747
Delta Electronics | E4-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 208 | 3.364 | CEC Inverter Database | 208V | Delta-Electronics-E4-TL-US(AC)-208V | Y | 1.23 | 0.33644 | 0.67288 | 1.0093 | 1.6822 | 2.5233 | 3.3644 | 95.4286 | 97.272 | 97.8821 | 98.254 | 98.3148 | 98.1972 | 94.8143 | 96.9329 | 97.6159 | 98.0971 | 98.1976 | 98.1162 | 93.9184 | 96.3871 | 97.1728 | 97.7982 | 97.993 | 97.934
Delta Electronics | E4-TL-US | Battery Inverter | 200 | 380 | 400 | 240 | 3.87 | CEC Inverter Database | 240V | Delta-Electronics-E4-TL-US-240V | Y | 1.27 | 0.38696 | 0.77392 | 1.1609 | 1.9348 | 2.9022 | 3.8696 | 92.8573 | 95.3032 | 96.0816 | 97.008 | 97.3433 | 97.3609 | 95.3025 | 97.1049 | 97.7261 | 98.0933 | 98.1429 | 98.1114 | 94.285 | 96.4536 | 97.2773 | 97.8608 | 98.0038 | 97.9448
Delta Electronics | E4-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 240 | 3.888 | CEC Inverter Database | 240V | Delta-Electronics-E4-TL-US(AC)-240V | Y | 1.28 | 0.38876 | 0.77751 | 1.1663 | 1.9438 | 2.9157 | 3.8876 | 95.9481 | 97.6144 | 98.153 | 98.4067 | 98.6146 | 98.3924 | 95.4757 | 97.3498 | 97.9766 | 98.3716 | 98.712 | 98.5177 | 94.657 | 96.7993 | 97.543 | 98.1036 | 98.616 | 98.4252
Delta Electronics | E6-TL-US | Battery Inverter | 200 | 380 | 480 | 208 | 4.992 | CEC Inverter Database | 208V | Delta-Electronics-E6-TL-US-208V | Y | 1.86 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94.0016 | 95.6485 | 96.4705 | 97.0318 | 96.9884 | 96.6789 | 95.696 | 97.2204 | 97.6522 | 97.8362 | 97.6671 | 97.3491 | 94.6317 | 96.517 | 97.1735 | 97.5416 | 97.4711 | 97.1739
Delta Electronics | E6-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 208 | 5 | CEC Inverter Database | 208V | Delta-Electronics-E6-TL-US(AC)-208V | Y | 1.85 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 94.7983 | 96.7769 | 97.4536 | 97.765 | 97.7211 | 97.431
Delta Electronics | E6-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 240 | 5 | CEC Inverter Database | 240V | Delta-Electronics-E6-TL-US(AC)-240V | Y | 2.05 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 94.8718 | 96.9341 | 97.5858 | 98.1949 | 98.1673 | 97.9672
Delta Electronics | E6-TL-US | Battery Inverter | 200 | 380 | 480 | 240 | 5.76 | CEC Inverter Database | 240V | Delta-Electronics-E6-TL-US-240V | Y | 2.25 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.9636 | 95.7324 | 96.5328 | 97.1183 | 97.0624 | 96.7746 | 96.2574 | 97.615 | 97.9819 | 98.0814 | 97.6804 | 97.6267 | 95.2386 | 96.9825 | 97.5357 | 97.8342 | 97.7548 | 97.4585
Delta Electronics | E8-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 240 | 6.494 | CEC Inverter Database | 240V | Delta-Electronics-E8-TL-US(AC)-240V | Y | 2.1 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.564 | 97.9534 | 98.1731 | 98.3825 | 98.2962 | 98.0856 | 95.9941 | 97.6828 | 98.1182 | 98.3712 | 98.3594 | 98.0923 | 95.036 | 97.1456 | 97.7444 | 98.1155 | 98.1782 | 97.9141
Delta Electronics | E8-TL-US(AC) | Battery Inverter | 350 | 400 | 480 | 208 | 6.5 | CEC Inverter Database | 208V | Delta-Electronics-E8-TL-US(AC)-208V | Y | 1.91 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.5268 | 97.8051 | 98.1607 | 98.2713 | 98.071 | 97.7448 | 95.9938 | 97.5402 | 97.9409 | 98.1437 | 97.9732 | 97.6535 | 95.0772 | 96.9768 | 97.5715 | 97.8841 | 97.7702 | 97.4644
Delta Electronics | E8-TL-US | Battery Inverter | 270 | 380 | 480 | 208 | 6.656 | CEC Inverter Database | 208V | Delta-Electronics-E8-TL-US-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2308 | 96.891 | 97.3835 | 97.6343 | 97.4276 | 97.0506 | 95.9476 | 97.4104 | 97.7946 | 97.9487 | 97.6997 | 97.3918 | 94.855 | 96.7763 | 97.3739 | 97.6604 | 97.5174 | 97.1621
Delta Electronics | E8-TL-US | Battery Inverter | 270 | 380 | 480 | 240 | 7.68 | CEC Inverter Database | 240V | Delta-Electronics-E8-TL-US-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2202 | 96.7865 | 97.3605 | 97.6615 | 97.5147 | 97.0633 | 96.5571 | 97.7682 | 98.0917 | 98.1644 | 97.9971 | 97.6404 | 95.5533 | 97.2136 | 97.7339 | 97.9476 | 97.8481 | 97.5018
Delta Electronics | E30-TL | Battery Inverter | 515 | 750 | 830 | 277 | 30.488 | CEC Inverter Database | 277V | Delta-Electronics-E30-TL-277V | Y | 1.59 | 3.0488 | 6.0975 | 9.1463 | 15.2438 | 22.8657 | 30.4876 | 95.9222 | 97.1353 | 97.5449 | 97.7515 | 97.701 | 97.4796 | 97.4461 | 98.3209 | 98.5555 | 98.6266 | 98.581 | 98.4647 | 96.9725 | 98.1055 | 98.382 | 98.4809 | 98.4516 | 98.3166
Delta Electronics | DES10JB125K01 | Battery Inverter | 750 | 900 | 1000 | 480 | 125 | CEC Inverter Database | 480V | Delta-Electronics-DES10JB125K01-480V | Y | 22.4 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 95.731 | 97.1982 | 97.5482 | 97.6472 | 97.4412 | 97.2142 | 93.8046 | 96.324 | 96.9331 | 97.278 | 97.2686 | 97.1169 | 92.3112 | 95.6622 | 96.4776 | 96.9704 | 97.0348 | 96.8004
Delta Electronics | PCS125 | Battery Inverter | 750 | 900 | 1000 | 480 | 125 | CEC Inverter Database | 480V | Delta-Electronics-PCS125-480V | Y | 22.4 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 95.731 | 97.1982 | 97.5482 | 97.6472 | 97.4412 | 97.2142 | 93.8046 | 96.324 | 96.9331 | 97.278 | 97.2686 | 97.1169 | 92.3112 | 95.6622 | 96.4776 | 96.9704 | 97.0348 | 96.8004
Delta Electronics | DWE2100-US | Battery Inverter | 760 | 900 | 1200 | 480 | 1887.74 | CEC Inverter Database | 480V | Delta-Electronics-DWE2100-US-480V | Y | 18.253 | 188.774 | 377.548 | 566.322 | 943.87 | 1415.805 | 1887.74 | 93.78 | 96.05 | 96.72 | 97.12 | 97.15 | 96.97 | 92.72 | 95.43 | 96.24 | 96.74 | 96.83 | 96.68 | 90.39 | 94.23 | 95.23 | 95.96 | 96.14 | 96.03
Delta Electronics | DWE2800-US | Battery Inverter | 760 | 900 | 1200 | 480 | 2513.388 | CEC Inverter Database | 480V | Delta-Electronics-DWE2800-US-480V | Y | 1114 | 251.3388 | 502.6776 | 754.0164 | 1256.694 | 1885.041 | 2513.388 | 93.9278 | 95.5206 | 96.4052 | 96.8951 | 96.9203 | 96.67 | 92.904 | 94.7314 | 95.8013 | 96.4366 | 96.5493 | 96.3786 | 90.6966 | 93.4081 | 94.7591 | 95.6698 | 95.8648 | 95.7398
DYNAPOWER COMPANY LLC | MPS-100 | Battery Inverter | 350 | 475 | 600 | 480 | 98.861 | CEC Inverter Database | 480V | DYNAPOWER-COMPANY-LLC-MPS-100-480V | Y | 803.97 | 9.8861 | 19.7722 | 29.6583 | 49.4305 | 74.1458 | 98.861 | 81.5497 | 89.9745 | 92.7648 | 95.0554 | 95.9538 | 96.2674 | 76.874 | 87.5246 | 90.7261 | 93.6858 | 95.0811 | 95.5789 | 73.018 | 84.9646 | 89.0409 | 92.3812 | 94.007 | 94.6159
DYNAPOWER COMPANY LLC | MPS-250 | Battery Inverter | 350 | 475 | 600 | 480 | 248.91 | CEC Inverter Database | 480V | DYNAPOWER-COMPANY-LLC-MPS-250-480V | Y | 1638.5 | 24.891 | 49.7812 | 74.6718 | 124.453 | 186.68 | 248.906 | 89.1 | 93.5 | 95 | 95.9 | 96 | 95.8 | 87.1 | 92.3 | 94.1 | 95.3 | 95.6 | 95.3 | 85.6 | 91.1 | 93 | 94.5 | 94.9 | 94.6
DYNAPOWER COMPANY LLC | MPS-250HV | Battery Inverter | 580 | 705 | 830 | 480 | 249.619 | CEC Inverter Database | 480V | DYNAPOWER-COMPANY-LLC-MPS-250HV-480V | Y | 437.7 | 24.9619 | 49.9238 | 74.8857 | 124.8095 | 187.2142 | 249.619 | 89.1625 | 93.2778 | 94.9436 | 96.6352 | 96.5073 | 96.4981 | 87.1443 | 92.741 | 94.1606 | 95.6894 | 96.3244 | 96.1982 | 86.2167 | 91.8394 | 93.7002 | 95.0852 | 95.7877 | 95.8819
DYNAPOWER COMPANY LLC | CPS-1500 Gen4 | Battery Inverter | 740 | 1000 | 1500 | 480 | 1199.64 | CEC Inverter Database | 480V | DYNAPOWER-COMPANY-LLC-CPS-1500-Gen4-480V | Y | 438.5 | 119.964 | 239.928 | 359.892 | 599.82 | 899.73 | 1199.64 | 95.1475 | 96.6264 | 97.0793 | 97.0011 | 96.684 | 96.1612 | 95.0089 | 96.2444 | 97.0385 | 96.8739 | 96.63 | 96.1664 | 95.054 | 95.9477 | 97.1667 | 96.6824 | 95.7593 | 96.1358
DYNAPOWER COMPANY LLC | CPS-1500 Gen4 | Battery Inverter | 900 | 1200 | 1500 | 600 | 1498.66 | CEC Inverter Database | 600V | DYNAPOWER-COMPANY-LLC-CPS-1500-Gen4-600V | Y | 1241 | 149.866 | 299.732 | 449.598 | 749.33 | 1123.995 | 1498.66 | 93.9516 | 95.1495 | 98.053 | 97.386 | 97.3516 | 97.084 | 93.453 | 94.8268 | 98.4238 | 97.4076 | 97.3745 | 97.0496 | 93.0695 | 94.5456 | 98.6194 | 97.4606 | 97.3881 | 96.9779
Enphase Energy Inc. | IQ8X-BAT-US | Battery Inverter | 52.5 | 63 | 73.5 | 240 | 0.318 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8X-BAT-US-240V | Y | 0.024 | 0.031776 | 0.063551 | 0.095327 | 0.15888 | 0.23832 | 0.31776 | 88.1194 | 93.9712 | 96.1546 | 97.3997 | 97.4828 | 97.2008 | 87.7712 | 93.4122 | 95.6873 | 97.1995 | 97.4368 | 97.2642 | 87.0694 | 92.8086 | 95.2929 | 96.9958 | 97.3087 | 97.1752
Enphase Energy Inc. | IQ8X-BAT-US-NB | Battery Inverter | 52.5 | 63 | 73.5 | 240 | 0.318 | CEC Inverter Database | 240V | Enphase-Energy-Inc.-IQ8X-BAT-US-NB-240V | Y | 0.024 | 0.031776 | 0.063551 | 0.095327 | 0.15888 | 0.23832 | 0.31776 | 88.1194 | 93.9712 | 96.1546 | 97.3997 | 97.4828 | 97.2008 | 87.7712 | 93.4122 | 95.6873 | 97.1995 | 97.4368 | 97.2642 | 87.0694 | 92.8086 | 95.2929 | 96.9958 | 97.3087 | 97.1752
EPC Power Corp. | HY LC12/6-7 | Battery Inverter | 455 | 475 | 600 | 480 | 220.033 | CEC Inverter Database | 480V | EPC-Power-Corp.-HY-LC12-6-7-480V | Y | 19.2 | 22.0033 | 44.0067 | 66.01 | 110.0167 | 165.025 | 220.0333 | 95.0157 | 96.16 | 96.4114 | 96.3571 | 96.0943 | 95.7657 | 93.9614 | 95.3957 | 95.6729 | 95.7343 | 95.5243 | 95.18 | 94.3386 | 95.8 | 96.0971 | 96.1657 | 96.0143 | 95.7186
EPC Power Corp. | 50-100122 | Battery Inverter | 710 | 950 | 1250 | 480 | 250.19 | CEC Inverter Database | 480V | EPC-Power-Corp.-50-100122-480V | Y | 20 | 25.019 | 50.038 | 75.057 | 125.095 | 187.643 | 250.19 | 94.8 | 96.79 | 97.38 | 97.66 | 97.6 | 97.44 | 94.12 | 96.48 | 97.08 | 97.37 | 97.29 | 97.04 | 92.55 | 95.64 | 96.52 | 96.95 | 96.97 | 96.78
EPC Power Corp. | 50-100205 | Battery Inverter | 710 | 950 | 1250 | 480 | 250.19 | CEC Inverter Database | 480V | EPC-Power-Corp.-50-100205-480V | Y | 20 | 25.019 | 50.038 | 75.057 | 125.095 | 187.643 | 250.19 | 94.8 | 96.79 | 97.38 | 97.66 | 97.6 | 97.44 | 94.12 | 96.48 | 97.08 | 97.37 | 97.29 | 97.04 | 92.55 | 95.64 | 96.52 | 96.95 | 96.97 | 96.78
EPC Power Corp. | 50-100100 | Battery Inverter | 400 | 700 | 1000 | 208 | 452.6 | CEC Inverter Database | 208V | EPC-Power-Corp.-50-100100-208V | Y | 0 | 45.26 | 90.52 | 135.78 | 226.3 | 339.45 | 452.6 | 94.6568 | 96.9294 | 97.2858 | 97.2732 | 96.0412 | 93.8658 | 92.5436 | 95.2824 | 96.104 | 96.3762 | 95.149 | 92.7892 | 90.0808 | 93.6788 | 94.7806 | 95.3118 | 94.371 | 92.6334
EPC Power Corp. | 50-100A-BCDEF-G | Battery Inverter | 710 | 950 | 1250 | 480 | 499.13 | CEC Inverter Database | 480V | EPC-Power-Corp.-50-100A-BCDEF-G-480V | Y | 20 | 49.913 | 99.826 | 149.739 | 249.565 | 374.3475 | 499.13 | 96.5303 | 97.7501 | 98.003 | 98.0553 | 97.9146 | 97.7354 | 96.0808 | 97.5448 | 97.8618 | 97.9256 | 97.7387 | 97.4688 | 93.7308 | 95.6096 | 96.015 | 96.1378 | 95.982 | 95.7344
EPC Power Corp. | 50-100100 | Battery Inverter | 750 | 1000 | 1250 | 480 | 1036.84 | CEC Inverter Database | 480V | EPC-Power-Corp.-50-100100-480V | Y | 0 | 103.684 | 207.368 | 311.052 | 518.42 | 777.63 | 1036.84 | 96.6166 | 98.1318 | 98.5074 | 98.6706 | 97.7058 | 95.8714 | 95.134 | 97.31 | 97.9136 | 98.2396 | 97.1842 | 95.0338 | 93.4078 | 96.4116 | 97.2556 | 97.7718 | 96.9296 | 95.129
EPC Power Corp. | 50-100100 | Battery Inverter | 1050 | 1150 | 1250 | 690 | 1499.86 | CEC Inverter Database | 690V | EPC-Power-Corp.-50-100100-690V | Y | 0 | 149.986 | 299.972 | 449.958 | 749.93 | 1124.895 | 1499.86 | 95.8536 | 98.1434 | 98.6344 | 98.8788 | 98.0058 | 96.3586 | 95.7388 | 97.7892 | 98.3848 | 98.733 | 97.9086 | 96.281 | 95.6382 | 97.6778 | 98.2602 | 98.588 | 97.7562 | 96.1748
GE Renewable Energy | RIU-2500-U | Battery Inverter | 800 | 975 | 1500 | 550 | 2507.194 | CEC Inverter Database | 550V | GE-Renewable-Energy-RIU-2500-U-550V | Y | 62.8 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426
Generac Power Systems | X7602 | Battery Inverter | 390 | 400 | 420 | 240 | 7.586 | CEC Inverter Database | 240V | Generac-Power-Systems-X7602-240V | Y | 1.2917 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91
Generac Power Systems | XVT076A03 | Battery Inverter | 390 | 400 | 420 | 240 | 7.839 | CEC Inverter Database | 240V | Generac-Power-Systems-XVT076A03-240V | Y | 1.29 | 0.78386 | 1.5677 | 2.3516 | 3.9193 | 5.879 | 7.8386 | 93.6776 | 95.9987 | 96.5326 | 97.2036 | 97.1603 | 97.1047 | 92.8234 | 95.6083 | 96.6681 | 97.2129 | 97.2231 | 97.1337 | 92.2887 | 95.332 | 96.1902 | 96.9866 | 97.13 | 97.0189
Generac Power Systems | X11402 | Battery Inverter | 390 | 400 | 420 | 208 | 11.18 | CEC Inverter Database | 208V | Generac-Power-Systems-X11402-208V | Y | 0.125 | 1.118 | 2.236 | 3.354 | 5.59 | 8.385 | 11.18 | 97.25 | 97.35 | 97.58 | 97.65 | 97.44 | 97.06 | 97.03 | 97.35 | 97.67 | 97.54 | 97.25 | 96.93 | 95.83 | 97.24 | 97.27 | 97.39 | 97.08 | 96.89
Generac Power Systems | XVT114G03 | Battery Inverter | 390 | 400 | 420 | 208 | 11.748 | CEC Inverter Database | 208V | Generac-Power-Systems-XVT114G03-208V | Y | 0.13 | 1.1748 | 2.3496 | 3.5243 | 5.8739 | 8.8109 | 11.7478 | 94.3952 | 96.3614 | 96.9844 | 97.3488 | 97.3913 | 97.3223 | 93.8375 | 96.116 | 96.8135 | 97.3003 | 97.2556 | 97.1149 | 92.9035 | 95.7659 | 96.54 | 97.0771 | 97.168 | 97.0658
Ginlong Technologies Co., Ltd. | RHI-1P5K-HVES-5G | Battery Inverter | 115 | 330 | 450 | 240 | 5.003 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P5K-HVES-5G-240V | Y | 1 | 0.5 | 1.001 | 1.501 | 2.501 | 3.752 | 5.003 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | RHI-1P6K-HVES-5G | Battery Inverter | 130 | 330 | 450 | 240 | 6.004 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P6K-HVES-5G-240V | Y | 1 | 0.6 | 1.201 | 1.801 | 3.002 | 4.503 | 6.004 | 94.9 | 96.12 | 96.76 | 97.3 | 97.32 | 96.48 | 95.55 | 96.98 | 97.4 | 97.42 | 97.37 | 97.95 | 95.31 | 96.91 | 97.48 | 97.59 | 97.58 | 97.58
Ginlong Technologies Co., Ltd. | RHI-1P7K-HVES-5G | Battery Inverter | 160 | 330 | 450 | 240 | 7.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P7K-HVES-5G-240V | Y | 1 | 0.701 | 1.401 | 2.102 | 3.503 | 5.254 | 7.006 | 94.96 | 96.16 | 96.83 | 97.36 | 97.35 | 96.54 | 95.58 | 97.01 | 97.43 | 97.5 | 97.51 | 97.04 | 95.32 | 96.96 | 97.52 | 97.66 | 97.6 | 97.6
Ginlong Technologies Co., Ltd. | RHI-1P7.6K-HVES-5G | Battery Inverter | 175 | 330 | 450 | 240 | 7.603 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P7.6K-HVES-5G-240V | Y | 1 | 0.76 | 1.521 | 2.281 | 3.801 | 5.702 | 7.603 | 95.05 | 96.16 | 96.89 | 97.34 | 97.15 | 96.58 | 95.63 | 97.18 | 97.48 | 97.78 | 97.35 | 97.9 | 95.36 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | RHI-1P8K-HVES-5G | Battery Inverter | 185 | 330 | 450 | 240 | 8.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P8K-HVES-5G-240V | Y | 1 | 0.801 | 1.601 | 2.402 | 4.003 | 6.004 | 8.006 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71
Ginlong Technologies Co., Ltd. | RHI-1P9K-HVES-5G | Battery Inverter | 210 | 330 | 450 | 240 | 9.006 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P9K-HVES-5G-240V | Y | 1 | 0.901 | 1.801 | 2.702 | 4.503 | 6.754 | 9.006 | 95.14 | 96.75 | 97 | 97.49 | 97.37 | 97 | 95.72 | 97.27 | 97.45 | 97.61 | 97.75 | 97.11 | 95.58 | 96.74 | 97.66 | 97.82 | 97.82 | 97.71
Ginlong Technologies Co., Ltd. | RHI-1P10K-HVES-5G | Battery Inverter | 230 | 330 | 450 | 240 | 10.005 | CEC Inverter Database | 240V | Ginlong-Technologies-Co.,-Ltd.-RHI-1P10K-HVES-5G-240V | Y | 1 | 1 | 2.001 | 3.001 | 5.002 | 7.504 | 10.005 | 95.18 | 96.78 | 97.08 | 97.55 | 97.61 | 97.06 | 95.3 | 96.32 | 97.58 | 97.66 | 97.73 | 97.21 | 95.6 | 96.8 | 97.68 | 97.79 | 97.81 | 97.71
Go Electric Inc. | 250-480-60-HLT | Battery Inverter | 540 | 700 | 780 | 480 | 259.2 | CEC Inverter Database | 480V | Go-Electric-Inc.-250-480-60-HLT-480V | Y | 748.7 | 25.92 | 51.84 | 77.76 | 129.6 | 194.4 | 259.2 | 80.3271 | 90.3414 | 93.4914 | 95.5014 | 95.0886 | 95.4071 | 78.96 | 88.09 | 91.61 | 93.81 | 94.57 | 94.5 | 76.6614 | 86.5629 | 90.2743 | 92.8071 | 93.6429 | 93.7629
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-6.0 | Battery Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-6.0-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
HANWHA Q CELLS AMERICA INC. | Q.HOME+ AC-G1-6.0 | Battery Inverter | 360 | 430 | 500 | 240 | 5.732 | CEC Inverter Database | 240V | HANWHA-Q-CELLS-AMERICA-INC.-Q.HOME+-AC-G1-6.0-240V | Y | 25 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-7.0 | Battery Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-7.0-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
HANWHA Q CELLS AMERICA INC. | Q.HOME+ AC-G1-7.0 | Battery Inverter | 280 | 390 | 500 | 240 | 6.68 | CEC Inverter Database | 240V | HANWHA-Q-CELLS-AMERICA-INC.-Q.HOME+-AC-G1-7.0-240V | Y | 25 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-7.6 | Battery Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-7.6-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
Hanwha Q CELLS America Inc. | Q.HOME+ AC-G1-7.6 | Battery Inverter | 320 | 375 | 430 | 240 | 7.832 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-AC-G1-7.6-240V | Y | 49.5 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369
Hanwha Q CELLS America Inc. | Q.HOME+ HYB-G1-8.6 | Battery Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-HYB-G1-8.6-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
Hanwha Q CELLS America Inc. | Q.HOME+ AC-G1-8.6 | Battery Inverter | 363 | 396.5 | 430 | 240 | 8.613 | CEC Inverter Database | 240V | Hanwha-Q-CELLS-America-Inc.-Q.HOME+-AC-G1-8.6-240V | Y | 42 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 610TL U B220 | Battery Inverter | 440 | 590 | 740 | 220 | 610 | CEC Inverter Database | 220V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-610TL-U-B220-220V | Y | 80 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 830TL U B300 | Battery Inverter | 440 | 590 | 740 | 300 | 830 | CEC Inverter Database | 300V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-830TL-U-B300-300V | Y | 80 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 915TL U B330 | Battery Inverter | 485 | 613 | 740 | 330 | 915 | CEC Inverter Database | 330V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-915TL-U-B330-330V | Y | 80 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1000TL U B360 | Battery Inverter | 524 | 632 | 740 | 360 | 1000 | CEC Inverter Database | 360V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1000TL-U-B360-360V | Y | 80 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1140TL U B410 | Battery Inverter | 595 | 668 | 800 | 410 | 1027.752 | CEC Inverter Database | 410V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1140TL-U-B410-410V | Y | 2550.2775 | 102.7752 | 205.5504 | 308.3256 | 513.876 | 770.814 | 1027.752 | 95.8625 | 97.4417 | 97.8113 | 97.8912 | 97.7441 | 97.3829 | 95.6736 | 97.3781 | 97.7557 | 97.8606 | 97.7193 | 97.3781 | 95.14 | 97.0801 | 97.524 | 97.6897 | 97.5561 | 97.213
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1245TL U B480 | Battery Inverter | 697 | 949 | 1200 | 480 | 1042.22 | CEC Inverter Database | 480V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1245TL-U-B480-480V | Y | 459.0724 | 104.222 | 208.444 | 312.666 | 521.11 | 781.665 | 1042.22 | 96.9037 | 97.6188 | 97.803 | 97.7395 | 97.5015 | 97.1174 | 96.4047 | 97.431 | 97.5993 | 97.4719 | 97.2822 | 96.859 | 96.026 | 97.0747 | 97.3979 | 97.2268 | 96.9903 | 96.5138
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1190TL U B430 | Battery Inverter | 624 | 682 | 800 | 430 | 1048.594 | CEC Inverter Database | 430V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1190TL-U-B430-430V | Y | 2550.2775 | 104.8594 | 209.7188 | 314.5782 | 524.297 | 786.4455 | 1048.594 | 96.0041 | 97.4811 | 97.8373 | 97.9231 | 97.7893 | 97.4138 | 95.8692 | 97.4303 | 97.7966 | 97.9039 | 97.781 | 97.4506 | 95.3825 | 97.1832 | 97.5935 | 97.7411 | 97.6496 | 97.3174
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1220TL U B440 | Battery Inverter | 638 | 689 | 800 | 440 | 1099.306 | CEC Inverter Database | 440V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1220TL-U-B440-440V | Y | 2550.2775 | 109.9306 | 219.8612 | 329.7918 | 549.653 | 824.4795 | 1099.306 | 95.932 | 97.4927 | 97.868 | 97.9487 | 97.8105 | 97.4537 | 95.8363 | 97.4652 | 97.8509 | 97.9442 | 97.8039 | 97.4677 | 95.4261 | 97.2395 | 97.6478 | 97.8037 | 97.6832 | 97.3514
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1110TL U B400 | Battery Inverter | 580 | 660 | 740 | 400 | 1110 | CEC Inverter Database | 400V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1110TL-U-B400-400V | Y | 80 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1250TL U B450 | Battery Inverter | 652 | 696 | 800 | 450 | 1114.104 | CEC Inverter Database | 450V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1250TL-U-B450-450V | Y | 2550.2775 | 111.4104 | 222.8208 | 334.2312 | 557.052 | 835.578 | 1114.104 | 95.9706 | 97.5016 | 97.8688 | 97.9364 | 97.8103 | 97.4968 | 95.9001 | 97.4837 | 97.855 | 97.9743 | 97.8316 | 97.5204 | 95.5073 | 97.2604 | 97.6982 | 97.8443 | 97.7172 | 97.4132
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1275TL U B460 | Battery Inverter | 666 | 703 | 800 | 460 | 1128.476 | CEC Inverter Database | 460V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1275TL-U-B460-460V | Y | 2550.2775 | 112.8476 | 225.6952 | 338.5428 | 564.238 | 846.357 | 1128.476 | 95.9938 | 97.508 | 97.8617 | 97.9706 | 97.8442 | 97.6278 | 95.8888 | 97.4823 | 97.8709 | 97.9916 | 97.8671 | 97.5597 | 95.5429 | 97.3202 | 97.7334 | 97.9123 | 97.7635 | 97.4905
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1165TL U B420 | Battery Inverter | 610 | 675 | 740 | 420 | 1165 | CEC Inverter Database | 420V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1165TL-U-B420-420V | Y | 80 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1740TL U B670 | Battery Inverter | 962 | 1081 | 1200 | 670 | 1272.412 | CEC Inverter Database | 670V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1740TL-U-B670-670V | Y | 459.0724 | 127.2412 | 254.4824 | 381.7236 | 636.206 | 954.309 | 1272.412 | 95.9646 | 97.3748 | 97.6902 | 97.7604 | 97.6287 | 97.348 | 95.7313 | 97.2879 | 97.5573 | 97.697 | 97.5442 | 97.223 | 95.3778 | 97.1365 | 97.419 | 97.506 | 97.402 | 97.144
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1800TL U B690 | Battery Inverter | 962 | 1081 | 1200 | 690 | 1300.644 | CEC Inverter Database | 690V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1800TL-U-B690-690V | Y | 459.0724 | 130.0644 | 260.1288 | 390.1932 | 650.322 | 975.483 | 1300.644 | 96.6717 | 97.6652 | 97.8788 | 97.9021 | 97.7538 | 97.399 | 96.4722 | 97.5961 | 97.804 | 97.828 | 97.6778 | 97.3356 | 96.3335 | 97.5145 | 97.7082 | 97.7346 | 97.5625 | 97.2579
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1665TL U B640 | Battery Inverter | 919 | 1060 | 1200 | 640 | 1367.076 | CEC Inverter Database | 640V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1665TL-U-B640-640V | Y | 459.0724 | 136.7076 | 273.4152 | 410.1228 | 683.538 | 1025.307 | 1367.076 | 96.2495 | 97.4423 | 97.7204 | 97.755 | 97.6184 | 97.3123 | 95.9772 | 97.3141 | 97.5906 | 97.6697 | 97.5061 | 97.1929 | 95.5155 | 97.1401 | 97.4064 | 97.4529 | 97.3426 | 97.0371
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1690TL U B650 | Battery Inverter | 933 | 1067 | 1200 | 650 | 1375.282 | CEC Inverter Database | 650V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1690TL-U-B650-650V | Y | 459.0724 | 137.5282 | 275.0564 | 412.5846 | 687.641 | 1031.4615 | 1375.282 | 96.2881 | 97.5051 | 97.7757 | 97.8183 | 97.6619 | 97.3581 | 96.0008 | 97.4016 | 97.6638 | 97.7405 | 97.5736 | 97.2501 | 95.6676 | 97.2627 | 97.5419 | 97.5575 | 97.4238 | 97.0851
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1715TL U B660 | Battery Inverter | 948 | 1074 | 1200 | 660 | 1390.614 | CEC Inverter Database | 660V | INGETEAM-POWER-TECHNOLOGY-S.A.-INGECON-SUN-1715TL-U-B660-660V | Y | 459.0724 | 139.0614 | 278.1228 | 417.1842 | 695.307 | 1042.9605 | 1390.614 | 96.0622 | 97.4034 | 97.6863 | 97.7536 | 97.622 | 97.3392 | 95.8419 | 97.2707 | 97.5502 | 97.7009 | 97.5384 | 97.2305 | 95.3647 | 97.1092 | 97.4005 | 97.5253 | 97.4034 | 97.0865
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000H-ES | Battery Inverter | 300 | 400 | 480 | 240 | 4.989 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000H-ES-240V | Y | 47.36 | 0.499 | 0.998 | 1.497 | 2.495 | 3.742 | 4.989 | 87.29 | 92.59 | 94.36 | 95.51 | 95.76 | 95.68 | 88.08 | 93.35 | 94.82 | 95.82 | 96.09 | 96.05 | 87.62 | 93.17 | 94.65 | 95.74 | 96.09 | 96.02
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 5.031 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000A-BP-240V | Y | 11.16 | 0.5031 | 1.0062 | 1.5093 | 2.5155 | 3.7732 | 5.031 | 92.3455 | 95.0391 | 95.888 | 96.374 | 96.441 | 96.3321 | 93.2413 | 95.834 | 96.4325 | 96.9776 | 97.1497 | 97.0738 | 92.0083 | 95.2827 | 96.1894 | 96.8065 | 96.9577 | 96.9254
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW5000A-ES | Battery Inverter | 300 | 400 | 480 | 240 | 5.0675 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW5000A-ES-240V | Y | 11.24 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW6000A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 6.03 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW6000A-BP-240V | Y | 11.3 | 0.603 | 1.206 | 1.809 | 3.015 | 4.5225 | 6.03 | 93.1771 | 95.286 | 96.0561 | 96.4195 | 96.3466 | 96.1346 | 93.9722 | 96.6306 | 96.6399 | 97.0392 | 97.0779 | 96.9108 | 93.5715 | 95.7069 | 96.4745 | 96.8879 | 96.9108 | 96.8052
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW6000A-ES | Battery Inverter | 360 | 400 | 480 | 240 | 6.109 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW6000A-ES-240V | Y | 9.3 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7000A-ES | Battery Inverter | 210 | 400 | 480 | 240 | 7.057 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7000A-ES-240V | Y | 9.48 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7000A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 7.059 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7000A-BP-240V | Y | 9.48 | 0.7059 | 1.4118 | 2.1177 | 3.5295 | 5.2942 | 7.059 | 94.1624 | 95.6808 | 96.2387 | 96.4556 | 96.2632 | 96.0229 | 94.8837 | 96.3856 | 96.6968 | 96.9955 | 97.0411 | 96.7889 | 93.4461 | 95.6865 | 96.4109 | 96.8452 | 96.8125 | 96.6488
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7600A-ES | Battery Inverter | 230 | 400 | 480 | 240 | 7.644 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7600A-ES-240V | Y | 9.44 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW7600A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 7.648 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW7600A-BP-240V | Y | 9.48 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 94.2091 | 95.7971 | 96.2502 | 96.4508 | 96.086 | 95.8884 | 95.3028 | 96.2388 | 96.7456 | 96.9702 | 96.8508 | 96.6381 | 93.7819 | 95.8515 | 96.4641 | 96.8137 | 96.743 | 96.552
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW8600A-ES | Battery Inverter | 260 | 400 | 480 | 240 | 8.614 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW8600A-ES-240V | Y | 9.54 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW8600A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 8.68 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW8600A-BP-240V | Y | 9.47 | 0.868 | 1.736 | 2.604 | 4.34 | 6.51 | 8.68 | 94.6958 | 96.0043 | 96.3343 | 96.3371 | 96.0115 | 95.6796 | 95.7573 | 96.48 | 96.9605 | 97.0225 | 96.9106 | 96.6148 | 94.6422 | 96.0768 | 96.4605 | 96.7395 | 96.7564 | 96.5087
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600H-ES | Battery Inverter | 300 | 400 | 480 | 240 | 9.519 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600H-ES-240V | Y | 45.22 | 0.9519 | 1.9038 | 2.8557 | 4.7595 | 7.1393 | 9.519 | 92.2072 | 94.7398 | 95.3899 | 95.5471 | 95.1557 | 94.5552 | 93.0285 | 95.4529 | 96.0211 | 96.1062 | 95.7384 | 95.1732 | 92.6051 | 95.1829 | 95.7232 | 95.9558 | 95.6413 | 94.9918
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600A-BP | Battery Inverter | 200 | 350 | 495 | 240 | 9.616 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600A-BP-240V | Y | 9.5 | 0.9616 | 1.9232 | 2.8848 | 4.808 | 7.212 | 9.616 | 95.0112 | 96.1034 | 96.3344 | 96.288 | 95.8601 | 95.4093 | 95.7041 | 96.6346 | 96.9842 | 96.9505 | 96.7684 | 96.4098 | 95.0504 | 96.1493 | 96.569 | 96.7048 | 96.6938 | 96.4008
Jiangsu Goodwe Power Supply Technology Co., LTD. | GW9600A-ES | Battery Inverter | 300 | 400 | 480 | 240 | 9.628 | CEC Inverter Database | 240V | Jiangsu-Goodwe-Power-Supply-Technology-Co.,-LTD.-GW9600A-ES-240V | Y | 9.4 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369
LG Electronics Inc. | A005KEEN261 | Battery Inverter | 350 | 400 | 450 | 208 | 5 | CEC Inverter Database | 208V | LG-Electronics-Inc.-A005KEEN261-208V | Y | 1.85 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 95.112 | 97.0074 | 97.61 | 97.87 | 97.8014 | 97.5053
LG Electronics Inc. | A005KEEN261 | Battery Inverter | 350 | 400 | 450 | 240 | 5 | CEC Inverter Database | 240V | LG-Electronics-Inc.-A005KEEN261-240V | Y | 2.05 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 95.244 | 97.1576 | 97.7531 | 98.2952 | 98.2453 | 98.0333
LG Electronics Inc. | D007KEEN261 | Battery Inverter | 270 | 380 | 450 | 208 | 6.656 | CEC Inverter Database | 208V | LG-Electronics-Inc.-D007KEEN261-208V | Y | 1.15 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 95.0392 | 96.9541 | 97.466 | 97.7308 | 97.5103 | 97.1462
LG Electronics Inc. | D007KEEN261 | Battery Inverter | 270 | 380 | 450 | 240 | 7.68 | CEC Inverter Database | 240V | LG-Electronics-Inc.-D007KEEN261-240V | Y | 1.19 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 95.7683 | 97.3217 | 97.8155 | 97.9581 | 97.748 | 97.4471
LS Energy Solutions LLC | PBE-6140-R61-1A0-1000 | Battery Inverter | 900 | 1125 | 1350 | 600 | 139.449 | CEC Inverter Database | 600V | LS-Energy-Solutions-LLC-PBE-6140-R61-1A0-1000-600V | Y | 1.58 | 13.9449 | 27.8898 | 41.8346 | 69.7244 | 104.5866 | 139.4488 | 97.4036 | 98.309 | 98.4912 | 98.7182 | 98.6138 | 98.533 | 96.7152 | 97.8982 | 98.2252 | 98.3488 | 98.378 | 98.282 | 96.0238 | 97.3794 | 97.74 | 98.0456 | 98.0902 | 98.0034
LS Energy Solutions LLC | PBE-5140-R61-1A0-1000 | Battery Inverter | 720 | 935 | 1150 | 480 | 140.485 | CEC Inverter Database | 480V | LS-Energy-Solutions-LLC-PBE-5140-R61-1A0-1000-480V | Y | 1.5 | 14.0485 | 28.097 | 42.1455 | 70.2425 | 105.3638 | 140.485 | 97.5 | 98.3658 | 98.4438 | 98.5204 | 98.4466 | 98.3362 | 96.596 | 97.653 | 97.9814 | 98.1558 | 98.0944 | 97.9973 | 95.592 | 97.1282 | 97.6164 | 97.7772 | 97.8094 | 97.6214
NeoVolta Inc. | NV7600 | Battery Inverter | 240 | 370 | 425 | 208 | 7.4473 | CEC Inverter Database | 208V | NeoVolta-Inc.-NV7600-208V | Y | 13.4 | 0.74473 | 1.4895 | 2.2342 | 3.7237 | 5.5855 | 7.4473 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631
NeoVolta Inc. | NV7600 | Battery Inverter | 240 | 370 | 425 | 240 | 7.657 | CEC Inverter Database | 240V | NeoVolta-Inc.-NV7600-240V | Y | 13.4 | 0.76571 | 1.5314 | 2.2971 | 3.8286 | 5.7428 | 7.6571 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868
OutBack Power Technologies, Inc. | FXR3048A | Battery Inverter | 40 | 52 | 60 | 120 | 2.56 | CEC Inverter Database | 120V | OutBack-Power-Technologies,-Inc.-FXR3048A-120V | Y | 0 | 0.26 | 0.51 | 0.77 | 1.28 | 1.92 | 2.56 | 83.7 | 90.2 | 92.2 | 93.3 | 92.6 | 91.6 | 79.8 | 87.1 | 90 | 92 | 92 | 91.2 | 77.3 | 85.1 | 88.1 | 90.6 | 91 | 90.7
OutBack Power Technologies, Inc. | VFXR3524A | Battery Inverter | 22 | 24 | 28 | 120 | 2.96 | CEC Inverter Database | 120V | OutBack-Power-Technologies,-Inc.-VFXR3524A-120V | Y | 0 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8
OutBack Power Technologies, Inc. | VFXR3648A | Battery Inverter | 40 | 51.2 | 60 | 120 | 3.037 | CEC Inverter Database | 120V | OutBack-Power-Technologies,-Inc.-VFXR3648A-120V | Y | 0 | 0.3 | 0.61 | 0.91 | 1.52 | 2.28 | 3.04 | 88 | 92.2 | 93.5 | 94 | 93 | 91.2 | 82.2 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 80.3 | 86.1 | 87.9 | 90.3 | 90.4 | 88.3
OutBack Power Technologies, Inc. | GS4048A | Battery Inverter | 44 | 48 | 56 | 240 | 3.6 | CEC Inverter Database | 240V | OutBack-Power-Technologies,-Inc.-GS4048A-240V | Y | 0.1 | 0.72 | 1.44 | 2.16 | 3.6 | 5.4 | 7.2 | 92.6 | 94.4 | 93.7 | 94.4 | 93 | 90.4 | 91.5 | 93.4 | 93 | 93.3 | 92.7 | 90.8 | 89 | 91.6 | 92.2 | 92.1 | 91.5 | 89.9
OutBack Power Technologies, Inc. | SBX5048-120/240 | Battery Inverter | 250 | 420 | 550 | 240 | 4.985 | CEC Inverter Database | 240V | OutBack-Power-Technologies,-Inc.-SBX5048-120-240-240V | Y | 24.85 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173
OutBack Power Technologies, Inc. | GS8048A | Battery Inverter | 44 | 48 | 56 | 240 | 7.2 | CEC Inverter Database | 240V | OutBack-Power-Technologies,-Inc.-GS8048A-240V | Y | 0.1 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.3 | 92.6 | 94.1 | 94.4 | 93.2 | 91.2 | 87.1 | 91.5 | 92.9 | 93.3 | 93 | 90.8 | 84 | 89 | 90.9 | 92.1 | 91.9 | 90.2
Oztek Corp. | OZPCS-RS40-Fxx | Battery Inverter | 550 | 700 | 820 | 208 | 17.515 | CEC Inverter Database | 208V | Oztek-Corp.-OZPCS-RS40-Fxx-208V | Y | 202.52 | 1.7515 | 3.5031 | 5.2546 | 8.7576 | 13.1365 | 17.5153 | 78.6327 | 88.4861 | 91.0734 | 92.8547 | 93.527 | 93.4074 | 82.2755 | 90.3116 | 92.0493 | 93.7198 | 93.9528 | 93.9222 | 84.9647 | 91.7444 | 92.925 | 94.1354 | 94.5961 | 94.2114
Oztek Corp. | OZPCS-RS40-Bxx | Battery Inverter | 550 | 700 | 820 | 208 | 17.516 | CEC Inverter Database | 208V | Oztek-Corp.-OZPCS-RS40-Bxx-208V | Y | 191.36 | 1.7516 | 3.5032 | 5.2549 | 8.7581 | 13.1371 | 17.5162 | 78.1631 | 89.2647 | 91.741 | 93.2416 | 93.8382 | 93.6886 | 81.2625 | 90.4785 | 92.8298 | 93.9721 | 94.3908 | 94.2223 | 84.6425 | 92.0011 | 93.4073 | 94.6493 | 94.8884 | 94.5526
Oztek Corp. | OZPCS-RS40-Fxx | Battery Inverter | 550 | 700 | 820 | 480 | 39.894 | CEC Inverter Database | 480V | Oztek-Corp.-OZPCS-RS40-Fxx-480V | Y | 1105.1 | 3.9894 | 7.9789 | 11.9683 | 19.9472 | 29.9208 | 39.8944 | 88.2974 | 93.8846 | 95.1099 | 96.1351 | 96.3208 | 96.2069 | 90.2558 | 94.5724 | 96.0317 | 96.673 | 96.7941 | 96.8675 | 91.3166 | 95.037 | 96.3475 | 97.0717 | 97.18 | 97.0126
Oztek Corp. | OZPCS-RS40-Bxx | Battery Inverter | 550 | 700 | 820 | 480 | 39.913 | CEC Inverter Database | 480V | Oztek-Corp.-OZPCS-RS40-Bxx-480V | Y | 1066.26 | 3.9913 | 7.9826 | 11.9739 | 19.9565 | 29.9347 | 39.913 | 89.3471 | 94.177 | 95.7028 | 96.5763 | 96.7765 | 96.5956 | 91.2397 | 94.7757 | 96.2649 | 97.0519 | 97.2428 | 97.1237 | 92.4802 | 95.5723 | 96.7908 | 97.4192 | 97.5042 | 97.4004
Pika Energy | X7602 | Battery Inverter | 390 | 400 | 420 | 240 | 7.587 | CEC Inverter Database | 240V | Pika-Energy-X7602-240V | Y | 1.29 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91
Pika Energy | X11402 | Battery Inverter | 390 | 400 | 420 | 208 | 11.187 | CEC Inverter Database | 208V | Pika-Energy-X11402-208V | Y | 0.13 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9
POMCube Inc. | PNZ-10K1N2-NA0 | Battery Inverter | 250 | 360 | 530 | 240 | 9.923 | CEC Inverter Database | 240V | POMCube-Inc.-PNZ-10K1N2-NA0-240V | Y | 21.92 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581
Power Electronics | FP3000K3 | Battery Inverter | 849 | 940 | 1200 | 600 | 3116.969 | CEC Inverter Database | 600V | Power-Electronics-FP3000K3-600V | Y | 442.59 | 311.6969 | 623.3938 | 935.0906 | 1558.484 | 2337.727 | 3116.969 | 96.023 | 97.7207 | 98.1252 | 98.386 | 98.2657 | 98.0531 | 95.9458 | 97.6341 | 98.0448 | 98.2818 | 98.158 | 97.9292 | 95.9202 | 97.6234 | 98.0333 | 98.2876 | 98.1723 | 97.9444
Power Electronics | FP3510M3 | Battery Inverter | 934 | 1000 | 1200 | 34500 | 3630.064 | CEC Inverter Database | 34500V | Power-Electronics-FP3510M3-34500V | Y | 7640 | 363.0064 | 726.0128 | 1089.0192 | 1815.032 | 2722.548 | 3630.064 | 95.0637 | 96.9102 | 97.5292 | 97.7902 | 97.755 | 96.9845 | 95.0013 | 96.8237 | 97.4321 | 97.6552 | 97.6302 | 96.8429 | 94.9968 | 96.7694 | 97.4072 | 97.704 | 97.6231 | 97.0263
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ-G1.3 | Battery Inverter | 540 | 750 | 830 | 480 | 29.444 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-30-WZZZZZZ-G1.3-480V | Y | 35.14 | 2.9444 | 5.8889 | 8.8333 | 14.7222 | 22.0832 | 29.4443 | 86.7633 | 92.621 | 93.1032 | 93.8163 | 93.2421 | 92.0854 | 87.6485 | 93.2657 | 93.53 | 94.1163 | 93.4041 | 92.9205 | 88.6063 | 92.4924 | 94.6691 | 94.5469 | 93.6549 | 93.0472
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZ-G1.3 | Battery Inverter | 540 | 750 | 830 | 480 | 29.956 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-30-ZZZZZZ-G1.3-480V | Y | 46.3 | 2.9956 | 5.9911 | 8.9867 | 14.9778 | 22.4667 | 29.9557 | 92.6541 | 95.1194 | 96.0767 | 96.8464 | 96.977 | 96.8538 | 93.7759 | 95.2415 | 96.5013 | 97.1768 | 97.3758 | 97.3985 | 92.7942 | 94.8855 | 96.3887 | 97.0579 | 97.1908 | 97.4251
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-G1.5 | Battery Inverter | 350 | 710 | 830 | 480 | 124.964 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-125XXXXXX-G1.5-480V | Y | 68 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 87.1196 | 92.9413 | 94.9723 | 95.2179 | 95.6593 | 95.2115 | 91.9189 | 95.3761 | 95.8979 | 96.6258 | 96.8865 | 96.649 | 91.5596 | 95.713 | 96.4245 | 96.9684 | 96.936 | 96.8929
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-W-G1.5 | Battery Inverter | 350 | 710 | 830 | 480 | 124.964 | CEC Inverter Database | 480V | Princeton-Power-Systems,-Inc.-GTIB-480-125XXXXXX-W-G1.5-480V | Y | 68 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 84.9387 | 91.6494 | 93.8422 | 94.0171 | 94.1574 | 93.2247 | 89.6179 | 94.0504 | 94.7567 | 95.4072 | 95.3654 | 94.6322 | 89.2675 | 94.3826 | 95.2771 | 95.7455 | 95.4141 | 94.8711
Rhombus Energy Solutions | BESI-50kW-480 | Battery Inverter | 550 | 636 | 840 | 480 | 49.35 | CEC Inverter Database | 480V | Rhombus-Energy-Solutions-BESI-50kW-480-480V | Y | 103 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 79 | 89 | 92 | 95 | 96 | 96 | 79 | 88.8571 | 92 | 94 | 96 | 96
Rhombus Energy Solutions | BESS-50kW-480 | Battery Inverter | 550 | 636 | 840 | 480 | 49.35 | CEC Inverter Database | 480V | Rhombus-Energy-Solutions-BESS-50kW-480-480V | Y | 103 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 79 | 89 | 92 | 95 | 96 | 96 | 79 | 88.8571 | 92 | 94 | 96 | 96
Rhombus Energy Solutions | RES-BESS60DP-480 | Battery Inverter | 270 | 441 | 870 | 480 | 59.789 | CEC Inverter Database | 480V | Rhombus-Energy-Solutions-RES-BESS60DP-480-480V | Y | 92 | 5.9789 | 11.9578 | 17.9367 | 29.8945 | 44.8418 | 59.789 | 82.328 | 88.79 | 91.344 | 93.2 | 93.729 | 93.632 | 81.46 | 87.412 | 90.408 | 92.422 | 93.1 | 93 | 79.44 | 86.038 | 88.894 | 91.278 | 92.026 | 92.06
Schneider Electric Solar Inc. | XW Pro 6848 NA | Battery Inverter | 47 | 52 | 58 | 120 | 5.747 | CEC Inverter Database | 120V | Schneider-Electric-Solar-Inc.-XW-Pro-6848-NA-120V | Y | 17.4 | 0.57472 | 1.1494 | 1.7242 | 2.8736 | 4.3104 | 5.7472 | 92.0582 | 94.5723 | 94.8034 | 94.5047 | 93.346 | 92.0348 | 91.8256 | 94.4642 | 94.7 | 94.4268 | 93.245 | 91.9758 | 91.6664 | 94.2323 | 94.5919 | 94.2474 | 93.1389 | 91.8939
Schneider Electric Solar Inc. | XW Pro 6848 NA | Battery Inverter | 47 | 52 | 58 | 240 | 6.019 | CEC Inverter Database | 240V | Schneider-Electric-Solar-Inc.-XW-Pro-6848-NA-240V | Y | 0.37 | 0.60185 | 1.2037 | 1.8056 | 3.0093 | 4.5139 | 6.0185 | 92.9291 | 94.4949 | 94.7555 | 95.18 | 93.909 | 92.2423 | 92.8245 | 94.4161 | 94.6733 | 95.15 | 93.8224 | 92.1594 | 92.703 | 94.3317 | 94.5539 | 95.0913 | 93.7217 | 92.0594
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3000TL-XH-US | Battery Inverter | 125 | 380 | 480 | 208 | 2.626 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3000TL-XH-US-208V | Y | 1.576 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3000TL BL-US | Battery Inverter | 150 | 380 | 480 | 240 | 2.934 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3000TL-BL-US-240V | Y | 15.128 | 0.29344 | 0.58687 | 0.88031 | 1.4672 | 2.2008 | 2.9344 | 83.5494 | 88.742 | 91.5187 | 93.466 | 94.3778 | 94.5735 | 82.9531 | 88.9774 | 91.284 | 94.7821 | 95.7609 | 95.9493 | 81.2489 | 86.9992 | 91.7283 | 93.6156 | 94.9487 | 95.5889
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3000TL BL-US | Battery Inverter | 150 | 380 | 480 | 208 | 2.999 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3000TL-BL-US-208V | Y | 15.128 | 0.29986 | 0.59972 | 0.89958 | 1.4993 | 2.249 | 2.9986 | 83.2934 | 88.7087 | 91.2183 | 93.3997 | 94.3355 | 94.6645 | 83.5823 | 88.3477 | 91.9042 | 94.2283 | 95.3991 | 95.8876 | 82.5038 | 87.6858 | 91.4301 | 93.8779 | 94.8499 | 95.7624
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3000TL-XH-US | Battery Inverter | 125 | 380 | 480 | 240 | 3.095 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3000TL-XH-US-240V | Y | 1.593 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3800TL-XH-US | Battery Inverter | 160 | 380 | 480 | 208 | 3.324 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3800TL-XH-US-208V | Y | 1.576 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3600TL BL-US | Battery Inverter | 150 | 380 | 480 | 208 | 3.581 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3600TL-BL-US-208V | Y | 15.128 | 0.3581 | 0.7162 | 1.0743 | 1.7905 | 2.6858 | 3.581 | 84.9552 | 90.4271 | 92.825 | 93.7968 | 94.5716 | 94.4365 | 85.0401 | 90.7332 | 93.4293 | 94.4908 | 95.7747 | 96.2727 | 82.3717 | 88.9668 | 92.9784 | 94.2953 | 95.7884 | 95.6672
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 3600TL BL-US | Battery Inverter | 150 | 380 | 480 | 240 | 3.608 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-3600TL-BL-US-240V | Y | 15.128 | 0.36084 | 0.72167 | 1.0825 | 1.8042 | 2.7063 | 3.6084 | 84.9226 | 90.0495 | 92.9079 | 93.7875 | 94.4318 | 94.456 | 84.8681 | 90.93 | 93.8567 | 94.562 | 95.5583 | 95.9727 | 82.4977 | 88.9887 | 92.2935 | 94.4687 | 94.7381 | 95.6144
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 3800TL-XH-US | Battery Inverter | 160 | 380 | 480 | 240 | 3.888 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-3800TL-XH-US-240V | Y | 1.593 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4000TL BL-US | Battery Inverter | 180 | 380 | 480 | 240 | 3.988 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4000TL-BL-US-240V | Y | 15.128 | 0.39884 | 0.79767 | 1.1965 | 1.9942 | 2.9913 | 3.9884 | 86.9226 | 91.0495 | 92.9079 | 94.5875 | 95.1318 | 95.156 | 86.5681 | 92.23 | 94.3567 | 95.662 | 96.2583 | 96.1727 | 84.4977 | 91.0887 | 93.3935 | 95.1687 | 96.1381 | 96.0144
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4000TL BL-US | Battery Inverter | 150 | 380 | 480 | 208 | 4.004 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4000TL-BL-US-208V | Y | 15.128 | 0.4004 | 0.8008 | 1.2012 | 2.002 | 3.003 | 4.004 | 86.7552 | 91.4271 | 93.125 | 94.3968 | 94.9716 | 95.2365 | 86.8401 | 92.1332 | 94.3293 | 95.6908 | 96.1747 | 96.1727 | 84.8717 | 91.2668 | 93.5784 | 95.1953 | 96.0884 | 96.0672
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 5000TL-XH-US | Battery Inverter | 210 | 380 | 480 | 208 | 4.28 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-5000TL-XH-US-208V | Y | 1.576 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4600TL BL-US | Battery Inverter | 180 | 380 | 480 | 240 | 4.598 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4600TL-BL-US-240V | Y | 15.128 | 0.45977 | 0.91955 | 1.3793 | 2.2989 | 3.4483 | 4.5977 | 86.9226 | 92.0495 | 93.3079 | 94.9095 | 95.2538 | 95.188 | 86.8681 | 92.43 | 94.5567 | 95.897 | 96.2323 | 96.2077 | 85.4977 | 91.4887 | 93.6035 | 95.4327 | 96.2821 | 96.1164
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 4600TL BL-US | Battery Inverter | 180 | 380 | 480 | 208 | 4.604 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-4600TL-BL-US-208V | Y | 15.128 | 0.4604 | 0.9208 | 1.3812 | 2.302 | 3.453 | 4.604 | 86.7552 | 91.6271 | 93.425 | 94.7968 | 95.1716 | 95.2365 | 87.8401 | 92.8332 | 94.7293 | 95.7908 | 96.2747 | 96.2727 | 85.8717 | 92.5668 | 94.0784 | 95.2953 | 96.3884 | 96.2672
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 5000TL-XH-US | Battery Inverter | 210 | 380 | 480 | 240 | 4.943 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-5000TL-XH-US-240V | Y | 1.593 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 5000TL BL-US | Battery Inverter | 230 | 380 | 480 | 240 | 4.954 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-5000TL-BL-US-240V | Y | 15.128 | 0.49537 | 0.99073 | 1.4861 | 2.4768 | 3.7153 | 4.9537 | 88.2674 | 92.0279 | 93.9177 | 95.1688 | 95.5976 | 95.4626 | 88.8274 | 93.6476 | 94.5929 | 96.1977 | 96.5262 | 95.9757 | 86.6548 | 92.4155 | 93.7005 | 95.5802 | 96.117 | 96.1089
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 5000TL BL-US | Battery Inverter | 230 | 380 | 480 | 208 | 4.969 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-5000TL-BL-US-208V | Y | 15.128 | 0.49688 | 0.99376 | 1.4906 | 2.4844 | 3.7266 | 4.9688 | 87.9969 | 91.8291 | 94.0292 | 95.277 | 95.6685 | 95.4968 | 88.6415 | 93.5556 | 94.7545 | 95.9536 | 96.5989 | 96.0872 | 87.0137 | 92.8034 | 93.5434 | 96.1629 | 96.0924 | 96.1985
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 6000TL-XH-US | Battery Inverter | 170 | 380 | 480 | 208 | 5.143 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-6000TL-XH-US-208V | Y | 1.576 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 6000TL BL-US | Battery Inverter | 230 | 380 | 480 | 208 | 5.232 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-6000TL-BL-US-208V | Y | 15.128 | 0.52322 | 1.0464 | 1.5697 | 2.6161 | 3.9242 | 5.2322 | 91.6216 | 94.3804 | 95.004 | 95.6415 | 95.648 | 95.6498 | 94.0058 | 96.3321 | 96.66 | 96.8442 | 96.8058 | 96.5216 | 93.9666 | 96.0001 | 96.4128 | 96.8643 | 96.7314 | 96.4957
Shenzhen Growatt New Energy Technology Co., Ltd | SPH 6000TL BL-US | Battery Inverter | 230 | 380 | 480 | 240 | 5.864 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-SPH-6000TL-BL-US-240V | Y | 15.128 | 0.58643 | 1.1729 | 1.7593 | 2.9322 | 4.3982 | 5.8643 | 91.5816 | 94.3604 | 94.954 | 95.5915 | 95.628 | 95.6398 | 93.9658 | 96.3021 | 96.58 | 96.8142 | 96.7558 | 96.5216 | 93.9266 | 95.9701 | 96.3828 | 96.8343 | 96.7114 | 96.4757
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 6000TL-XH-US | Battery Inverter | 170 | 380 | 480 | 240 | 5.918 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-6000TL-XH-US-240V | Y | 1.593 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 7600TL-XH-US | Battery Inverter | 212 | 380 | 480 | 208 | 6.58 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-7600TL-XH-US-208V | Y | 1.576 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US | Battery Inverter | 250 | 380 | 480 | 208 | 7.166 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-8200TL-XH-US-208V | Y | 10 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 7600TL-XH-US | Battery Inverter | 212 | 380 | 480 | 240 | 7.524 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-7600TL-XH-US-240V | Y | 1.593 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US | Battery Inverter | 250 | 380 | 480 | 208 | 7.874 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-9000TL-XH-US-208V | Y | 10 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 8200TL-XH-US | Battery Inverter | 250 | 380 | 480 | 240 | 8.251 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-8200TL-XH-US-240V | Y | 10 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US | Battery Inverter | 250 | 380 | 480 | 208 | 8.76 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-10000TL-XH-US-208V | Y | 10 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 9000TL-XH-US | Battery Inverter | 250 | 380 | 480 | 240 | 9.063 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-9000TL-XH-US-240V | Y | 10 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US | Battery Inverter | 250 | 380 | 480 | 208 | 10.04 | CEC Inverter Database | 208V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-11400TL-XH-US-208V | Y | 10 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 10000TL-XH-US | Battery Inverter | 250 | 380 | 480 | 240 | 10.082 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-10000TL-XH-US-240V | Y | 10 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719
Shenzhen Growatt New Energy Technology Co., Ltd | MIN 11400TL-XH-US | Battery Inverter | 250 | 380 | 480 | 240 | 11.52 | CEC Inverter Database | 240V | Shenzhen-Growatt-New-Energy-Technology-Co.,-Ltd-MIN-11400TL-XH-US-240V | Y | 10 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582
Shenzhen Sinexcel Electric Co., Ltd | PWS2-30K-NA | Battery Inverter | 350 | 600 | 750 | 480 | 30.02 | CEC Inverter Database | 480V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS2-30K-NA-480V | Y | 1.857 | 3.002 | 6.004 | 9.006 | 15.01 | 22.515 | 30.02 | 91.2328 | 94.2776 | 95.1804 | 95.6343 | 95.5611 | 95.1895 | 94.0804 | 95.9185 | 96.6069 | 97.0086 | 97.0306 | 96.8722 | 94.9891 | 96.635 | 97.1812 | 97.4446 | 97.4471 | 97.2664
Shenzhen Sinexcel Electric Co., Ltd | PWS1-50K-NA | Battery Inverter | 500 | 650 | 850 | 480 | 48.58 | CEC Inverter Database | 480V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS1-50K-NA-480V | Y | 860 | 4.858 | 9.716 | 14.574 | 24.29 | 36.435 | 48.58 | 87.3239 | 92.4174 | 93.9642 | 94.911 | 94.9348 | 94.6249 | 86.4796 | 91.8343 | 93.5215 | 94.5382 | 94.6245 | 94.3137 | 85.5066 | 91.2148 | 92.8921 | 94.1271 | 94.1483 | 93.9232
Shenzhen Sinexcel Electric Co., Ltd | PWS1-100K-NA | Battery Inverter | 500 | 650 | 850 | 480 | 98.013 | CEC Inverter Database | 480V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS1-100K-NA-480V | Y | 997 | 9.8013 | 19.6026 | 29.4039 | 49.0065 | 73.5097 | 98.013 | 87.3115 | 92.4599 | 94.0486 | 95.0349 | 95.1062 | 94.7968 | 86.5716 | 91.9322 | 93.5785 | 94.5421 | 94.644 | 94.3807 | 85.5959 | 91.2784 | 92.9994 | 94.0717 | 94.2626 | 94.044
Shenzhen Sinexcel Electric Co., Ltd | PWS1-150K-NA | Battery Inverter | 500 | 650 | 850 | 480 | 147.47 | CEC Inverter Database | 480V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS1-150K-NA-480V | Y | 1360 | 14.747 | 29.494 | 44.241 | 73.735 | 110.6025 | 147.47 | 88.5911 | 93.0981 | 94.4501 | 95.1722 | 95.219 | 94.8928 | 87.8328 | 92.6191 | 94.0834 | 94.9672 | 95.0226 | 94.7007 | 86.7442 | 91.8963 | 93.4554 | 94.3477 | 94.4727 | 94.2361
Shenzhen Sinexcel Electric Co., Ltd | PWS1-250K-NA | Battery Inverter | 500 | 650 | 850 | 480 | 244.026 | CEC Inverter Database | 480V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS1-250K-NA-480V | Y | 1860 | 24.4026 | 48.8052 | 73.2078 | 122.013 | 183.0195 | 244.026 | 91.3922 | 94.968 | 95.7012 | 96.033 | 95.7801 | 95.4154 | 90.4456 | 94.3962 | 95.2142 | 95.5745 | 95.3838 | 95.0192 | 89.2163 | 93.5746 | 94.5987 | 95.0795 | 94.9604 | 94.63
Shenzhen Sinexcel Electric Co., Ltd | PWS1-500KTL-NA | Battery Inverter | 640 | 750 | 900 | 400 | 498.34 | CEC Inverter Database | 400V | Shenzhen-Sinexcel-Electric-Co.,-Ltd-PWS1-500KTL-NA-400V | Y | 289.9 | 49.83 | 99.67 | 149.5 | 249.17 | 373.76 | 498.34 | 93.95 | 96 | 96.6 | 96.83 | 96.64 | 96.31 | 93.16 | 95.61 | 96.3 | 96.61 | 96.47 | 96.13 | 92.19 | 95.03 | 95.86 | 96.27 | 96.14 | 95.84
SMA America | SBS3.8-US-10 | Battery Inverter | 220 | 360 | 550 | 240 | 3.8 | CEC Inverter Database | 240V | SMA-America-SBS3.8-US-10-240V | Y | 6.53 | 0.38129 | 0.76257 | 1.1439 | 1.9064 | 2.8596 | 3.8129 | 92.6936 | 95.522 | 96.0988 | 96.4348 | 96.4124 | 96.2874 | 93.606 | 96.4562 | 97.1022 | 97.4216 | 97.4656 | 97.3776 | 88.5644 | 94.7228 | 96.0868 | 96.8482 | 97.0258 | 97.0206
SMA America | SBS5.0-US-10 | Battery Inverter | 220 | 360 | 550 | 240 | 5 | CEC Inverter Database | 240V | SMA-America-SBS5.0-US-10-240V | Y | 6.53 | 0.5016 | 1.0032 | 1.5048 | 2.508 | 3.762 | 5.016 | 93.7572 | 95.9944 | 96.3534 | 96.4338 | 96.3082 | 96.1104 | 94.6136 | 96.9314 | 97.3164 | 97.4512 | 97.3954 | 97.2108 | 92.4176 | 95.7396 | 96.5304 | 96.9972 | 97.034 | 96.5908
SMA America | SBS6.0-US-10 | Battery Inverter | 220 | 360 | 550 | 240 | 6 | CEC Inverter Database | 240V | SMA-America-SBS6.0-US-10-240V | Y | 6.53 | 0.6022 | 1.2044 | 1.8066 | 3.011 | 4.5165 | 6.022 | 94.4642 | 96.1546 | 96.429 | 96.4004 | 96.1916 | 95.9566 | 95.8482 | 97.1984 | 97.4014 | 97.4512 | 97.284 | 96.9922 | 93.2534 | 96.2388 | 96.799 | 97.0266 | 96.9664 | 96.8002
SMA America | SCS 2475-US | Battery Inverter | 577 | 673 | 950 | 385 | 2078.89 | CEC Inverter Database | 385V | SMA-America-SCS-2475-US-385V | Y | 297 | 207.889 | 415.778 | 623.667 | 1039.445 | 1559.168 | 2078.89 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18
SMA America | SC 4000 UP-US 600V 3850A | Battery Inverter | 880 | 970 | 1200 | 600 | 3650.134 | CEC Inverter Database | 600V | SMA-America-SC-4000-UP-US-600V-3850A-600V | Y | 453.5 | 365.0134 | 730.0268 | 1095.0402 | 1825.067 | 2737.6005 | 3650.134 | 98.2807 | 98.7001 | 98.7205 | 98.6249 | 98.4911 | 98.1606 | 98.0525 | 98.5891 | 98.6273 | 98.5552 | 98.3953 | 98.0229 | 97.3227 | 98.2881 | 98.4129 | 98.4176 | 98.2202 | 97.8437
SMA America | SC 4200 UP-US 630V 3850A | Battery Inverter | 921 | 1001 | 1200 | 630 | 3832.828 | CEC Inverter Database | 630V | SMA-America-SC-4200-UP-US-630V-3850A-630V | Y | 451.8 | 383.2828 | 766.5656 | 1149.8484 | 1916.414 | 2874.621 | 3832.828 | 98.2694 | 98.7021 | 98.6674 | 98.6466 | 98.5287 | 98.2119 | 97.9903 | 98.5997 | 98.6622 | 98.5939 | 98.4546 | 98.0872 | 97.504 | 98.3658 | 98.3947 | 98.4009 | 98.3081 | 97.9519
SMA America | SC 4400 UP-US 660V 3850A | Battery Inverter | 962 | 1032 | 1200 | 660 | 4017.113 | CEC Inverter Database | 660V | SMA-America-SC-4400-UP-US-660V-3850A-660V | Y | 465.17 | 401.7113 | 803.4226 | 1205.1339 | 2008.5565 | 3012.8347 | 4017.113 | 98.287 | 98.7337 | 98.7105 | 98.7078 | 98.6023 | 98.295 | 98.1038 | 98.6371 | 98.6292 | 98.6406 | 98.5024 | 98.149 | 97.5982 | 98.4496 | 98.5884 | 98.4873 | 98.3886 | 98.0401
SMA America | SC 4600 UP-US 690V 3850A | Battery Inverter | 1003 | 1062 | 1200 | 690 | 4198.235 | CEC Inverter Database | 690V | SMA-America-SC-4600-UP-US-690V-3850A-690V | Y | 471.07 | 419.8235 | 839.647 | 1259.4705 | 2099.1175 | 3148.6762 | 4198.235 | 98.2728 | 98.7421 | 98.7243 | 98.7352 | 98.6471 | 98.3477 | 98.1499 | 98.6747 | 98.6863 | 98.6911 | 98.5653 | 98.2147 | 97.7407 | 98.5298 | 98.644 | 98.5955 | 98.4551 | 98.1264
SolarEdge Technologies Ltd. | SE3000H-US | Battery Inverter | 360 | 395 | 480 | 240 | 2.962 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3000H-US-240V | Y | 0 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17
SolarEdge Technologies Ltd. | SE3800H-US | Battery Inverter | 360 | 395 | 480 | 240 | 3.747 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3800H-US-240V | Y | 0 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08
SolarEdge Technologies Ltd. | SE3800A-US | Battery Inverter | 360 | 400 | 480 | 240 | 3.79 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE3800A-US-240V | Y | 2.24 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8
SolarEdge Technologies Ltd. | SE6000H-US | Battery Inverter | 360 | 395 | 480 | 240 | 6.046 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE6000H-US-240V | Y | 4.52 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71
SolarEdge Technologies Ltd. | SE7600H-US | Battery Inverter | 360 | 395 | 480 | 240 | 7.616 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE7600H-US-240V | Y | 4.52 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71
SolarEdge Technologies Ltd. | SE7600A-US | Battery Inverter | 360 | 400 | 480 | 240 | 7.625 | CEC Inverter Database | 240V | SolarEdge-Technologies-Ltd.-SE7600A-US-240V | Y | 2.16 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1
SolarJuice American Inc. | S4A-H60 | Battery Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H60-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
SolarJuice American Inc. | S4A-A60 | Battery Inverter | 360 | 430 | 500 | 240 | 5.732 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-A60-240V | Y | 25 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094
SolarJuice American Inc. | S4A-H70 | Battery Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H70-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
SolarJuice American Inc. | S4A-A70 | Battery Inverter | 280 | 390 | 500 | 240 | 6.68 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-A70-240V | Y | 25 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733
SolarJuice American Inc. | S4A-H76 | Battery Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H76-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
SolarJuice American Inc. | S4A-A76 | Battery Inverter | 320 | 375 | 430 | 240 | 7.832 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-A76-240V | Y | 49.5 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369
SolarJuice American Inc. | S4A-H86 | Battery Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-H86-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
SolarJuice American Inc. | S4A-A86 | Battery Inverter | 363 | 396.5 | 430 | 240 | 8.613 | CEC Inverter Database | 240V | SolarJuice-American-Inc.-S4A-A86-240V | Y | 42 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524
Sol-Ark | Sol-Ark-8k-48-ST | Battery Inverter | 240 | 370 | 425 | 208 | 7.839 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-8k-48-ST-208V | Y | 13.4 | 0.78393 | 1.5679 | 2.3518 | 3.9196 | 5.8795 | 7.8393 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631
Sol-Ark | Sol-Ark-8k-48-ST | Battery Inverter | 240 | 370 | 425 | 240 | 7.976 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-8k-48-ST-240V | Y | 13.4 | 0.79762 | 1.5952 | 2.3928 | 3.9881 | 5.9821 | 7.9762 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868
Sol-Ark | Sol-Ark-12K-P | Battery Inverter | 240 | 370 | 425 | 208 | 8.818 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-12K-P-208V | Y | 13.4 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098
Sol-Ark | Sol-Ark-9k-48-ST | Battery Inverter | 240 | 370 | 425 | 208 | 8.818 | CEC Inverter Database | 208V | Sol-Ark-Sol-Ark-9k-48-ST-208V | Y | 13.4 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098
Sol-Ark | Sol-Ark-12K-P | Battery Inverter | 240 | 370 | 425 | 240 | 8.982 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-12K-P-240V | Y | 13.4 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494
Sol-Ark | Sol-Ark-9k-48-ST | Battery Inverter | 240 | 370 | 425 | 240 | 8.982 | CEC Inverter Database | 240V | Sol-Ark-Sol-Ark-9k-48-ST-240V | Y | 13.4 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-6.0-US | Battery Inverter | 240 | 335 | 425 | 240 | 5.57 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-6.0-US-240V | Y | 25 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-6.0-US | Battery Inverter | 360 | 430 | 500 | 240 | 5.732 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Fit-6.0-US-240V | Y | 25 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.0-US | Battery Inverter | 290 | 360 | 425 | 240 | 6.666 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-7.0-US-240V | Y | 25 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-7.0-US | Battery Inverter | 280 | 390 | 500 | 240 | 6.68 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Fit-7.0-US-240V | Y | 25 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.6-US | Battery Inverter | 304 | 402 | 500 | 240 | 7.642 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-7.6-US-240V | Y | 44 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-7.6-US | Battery Inverter | 320 | 375 | 430 | 240 | 7.832 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Fit-7.6-US-240V | Y | 49.5 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-8.6-US | Battery Inverter | 258 | 379 | 500 | 240 | 8.604 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Hybrid-8.6-US-240V | Y | 40 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-8.6-US | Battery Inverter | 363 | 396.5 | 430 | 240 | 8.613 | CEC Inverter Database | 240V | SolaX-Power-Network-Technology-(Zhe-jiang)-Co.,-Ltd.-A1-Fit-8.6-US-240V | Y | 42 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524
Sungrow Power Supply Co., Ltd. | SC60HV | Battery Inverter | 700 | 850 | 1300 | 480 | 66 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SC60HV-480V | Y | 0.26 | 6.6281 | 13.2561 | 19.8842 | 33.1404 | 49.7105 | 66.2807 | 97.3638 | 98.2989 | 98.5712 | 98.5281 | 98.3286 | 98.1691 | 96.7215 | 97.825 | 98.1342 | 98.1458 | 98.0383 | 97.8359 | 94.5379 | 96.5379 | 97.2009 | 97.5021 | 97.4648 | 97.3043
Sungrow Power Supply Co., Ltd. | SC75HV | Battery Inverter | 870 | 1000 | 1300 | 600 | 82.5 | CEC Inverter Database | 600V | Sungrow-Power-Supply-Co.,-Ltd.-SC75HV-600V | Y | 5.35 | 8.2568 | 16.5137 | 24.7705 | 41.2842 | 61.9263 | 82.5684 | 97.5289 | 98.3356 | 98.5333 | 98.5931 | 98.4281 | 98.2689 | 96.8742 | 97.9804 | 98.2077 | 98.2667 | 98.1351 | 97.9228 | 94.7732 | 97.15 | 97.6049 | 97.8392 | 97.7759 | 97.5738
Sungrow Power Supply Co., Ltd. | SG250HX-US | Battery Inverter | 860 | 1080 | 1300 | 800 | 226.997 | CEC Inverter Database | 800V | Sungrow-Power-Supply-Co.,-Ltd.-SG250HX-US-800V | Y | 5.21 | 22.6997 | 45.3994 | 68.0992 | 113.4986 | 170.2479 | 226.9972 | 97.0577 | 98.2506 | 98.469 | 98.5708 | 98.4621 | 98.262 | 98.195 | 98.7627 | 98.9461 | 99.0101 | 98.869 | 98.6779 | 97.9983 | 98.6612 | 98.8997 | 98.9478 | 98.8178 | 98.632
Sungrow Power Supply Co., Ltd. | SC250KU | Battery Inverter | 500 | 675 | 850 | 480 | 250 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SC250KU-480V | Y | 93.64 | 25.329 | 50.6581 | 75.9871 | 126.6452 | 189.9678 | 253.2904 | 95.0019 | 96.5561 | 96.9221 | 96.7419 | 96.3008 | 95.8054 | 94.0209 | 96.3064 | 96.5163 | 96.3454 | 96.1902 | 95.7691 | 92.8571 | 94.8975 | 96.0999 | 96.0222 | 95.9534 | 95.5741
Sungrow Power Supply Co., Ltd. | SC1000KU | Battery Inverter | 810 | 1005 | 1200 | 540 | 1001.306 | CEC Inverter Database | 540V | Sungrow-Power-Supply-Co.,-Ltd.-SC1000KU-540V | Y | 83.7646 | 100.1306 | 200.2612 | 300.3918 | 500.653 | 750.9795 | 1001.306 | 94.9956 | 96.8144 | 97.2437 | 97.3155 | 97.0286 | 96.6633 | 94.2811 | 96.3444 | 96.9047 | 97.0479 | 96.8017 | 96.439 | 93.6894 | 95.9275 | 96.5802 | 96.8324 | 96.5978 | 96.1882
Sungrow Power Supply Co., Ltd. | SC1200UD-US | Battery Inverter | 700 | 900 | 1500 | 480 | 1203.052 | CEC Inverter Database | 480V | Sungrow-Power-Supply-Co.,-Ltd.-SC1200UD-US-480V | Y | 146.929 | 120.3052 | 240.6104 | 360.9156 | 601.526 | 902.289 | 1203.052 | 98.4881 | 98.7829 | 98.7942 | 98.6273 | 98.3268 | 98.0578 | 98.1743 | 98.5753 | 98.598 | 98.4816 | 98.2181 | 97.9451 | 97.2336 | 98.0029 | 98.2153 | 98.2283 | 98.015 | 97.7698
Sungrow Power Supply Co., Ltd. | SC1375UD-US | Battery Inverter | 800 | 975 | 1500 | 550 | 1378.936 | CEC Inverter Database | 550V | Sungrow-Power-Supply-Co.,-Ltd.-SC1375UD-US-550V | Y | 144.254 | 137.8936 | 275.7872 | 413.6808 | 689.468 | 1034.202 | 1378.936 | 98.4972 | 98.8173 | 98.8873 | 98.7562 | 98.5195 | 98.2335 | 98.2871 | 98.7125 | 98.7893 | 98.6739 | 98.4481 | 98.1471 | 97.6928 | 98.3328 | 98.4872 | 98.4032 | 98.2035 | 98.0163
Sungrow Power Supply Co., Ltd. | SC1575UD-US | Battery Inverter | 915 | 1062 | 1500 | 630 | 1582.996 | CEC Inverter Database | 630V | Sungrow-Power-Supply-Co.,-Ltd.-SC1575UD-US-630V | Y | 144.104 | 158.2996 | 316.5992 | 474.8988 | 791.498 | 1187.247 | 1582.996 | 98.5171 | 98.8728 | 98.9565 | 98.8432 | 98.6696 | 98.308 | 98.2726 | 98.7726 | 98.8628 | 98.7828 | 98.5989 | 98.2712 | 97.8901 | 98.4771 | 98.6428 | 98.5894 | 98.4413 | 98.1299
Sungrow Power Supply Co., Ltd. | SC1725UD-US | Battery Inverter | 1000 | 1125 | 1500 | 690 | 1728.406 | CEC Inverter Database | 690V | Sungrow-Power-Supply-Co.,-Ltd.-SC1725UD-US-690V | Y | 141.725 | 172.8406 | 345.6812 | 518.5218 | 864.203 | 1296.3045 | 1728.406 | 98.5057 | 98.8927 | 99.016 | 98.9552 | 98.7298 | 98.4459 | 98.2439 | 98.782 | 98.9046 | 98.8565 | 98.6774 | 98.346 | 97.958 | 98.595 | 98.7454 | 98.7257 | 98.5906 | 98.2302
Sungrow Power Supply Co., Ltd. | SC2500U | Battery Inverter | 800 | 975 | 1500 | 550 | 2507.194 | CEC Inverter Database | 550V | Sungrow-Power-Supply-Co.,-Ltd.-SC2500U-550V | Y | 62.8 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426
Tabuchi Electric Co., Ltd. | THD-S55P3BB-US | Battery Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THD-S55P3BB-US-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9
Tabuchi Electric Co., Ltd. | THD-S55P3B-US | Battery Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THD-S55P3B-US-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9
Tabuchi Electric Co., Ltd. | THE-S55P3BB-USW | Battery Inverter | 240 | 380 | 520 | 240 | 5.5189 | CEC Inverter Database | 240V | Tabuchi-Electric-Co.,-Ltd.-THE-S55P3BB-USW-240V | Y | 10.1 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.326 | 93.286 | 94.304 | 94.656 | 94.048 | 94.174 | 89.688 | 93.666 | 94.706 | 95.44 | 95.498 | 95.41 | 88.78 | 93.076 | 94.276 | 95.094 | 95.166 | 94.922
WSTECH GmbH | APS800-ES-1-440-5 | Battery Inverter | 648 | 1000 | 1500 | 440 | 814.167 | CEC Inverter Database | 440V | WSTECH-GmbH-APS800-ES-1-440-5-440V | Y | 91.4 | 81.4167 | 162.8334 | 244.2501 | 407.0835 | 610.6252 | 814.1669 | 96.8994 | 97.9207 | 98.1472 | 98.0855 | 97.7317 | 97.3005 | 97.156 | 97.9031 | 98.0845 | 97.9812 | 97.697 | 97.2751 | 96.5182 | 97.3518 | 97.6259 | 97.6679 | 97.3419 | 96.9571
WSTECH GmbH | APS870-ES-1-480-5 | Battery Inverter | 770 | 1000 | 1470 | 480 | 872.029 | CEC Inverter Database | 480V | WSTECH-GmbH-APS870-ES-1-480-5-480V | Y | 91.402 | 87.2029 | 174.4058 | 261.6087 | 436.0145 | 654.0218 | 872.029 | 97.0815 | 98.1883 | 98.4162 | 98.4017 | 98.1322 | 97.7562 | 95.7664 | 97.2807 | 97.8339 | 98.0408 | 97.8593 | 97.5271 | 96.9374 | 97.6397 | 97.8465 | 97.7946 | 97.5592 | 97.1756
WSTECH GmbH | APS1600-ES-2-440-5 | Battery Inverter | 648 | 1000 | 1500 | 440 | 1626.952 | CEC Inverter Database | 440V | WSTECH-GmbH-APS1600-ES-2-440-5-440V | Y | 91.4 | 162.6952 | 325.3904 | 488.0856 | 813.476 | 1220.214 | 1626.952 | 98.0396 | 98.5839 | 98.6684 | 98.5329 | 98.2151 | 97.8585 | 96.9836 | 97.9106 | 98.1157 | 98.1085 | 97.8527 | 97.453 | 96.318 | 97.3792 | 97.6608 | 97.7017 | 97.437 | 97.0028
WSTECH GmbH | APS1740-ES-2-480-5 | Battery Inverter | 770 | 1000 | 1470 | 480 | 1735.36 | CEC Inverter Database | 480V | WSTECH-GmbH-APS1740-ES-2-480-5-480V | Y | 91.402 | 173.536 | 347.0721 | 520.6081 | 867.6802 | 1301.5204 | 1735.3605 | 96.2018 | 97.6354 | 98.0243 | 98.1239 | 97.9169 | 97.5975 | 95.6963 | 97.2746 | 97.7805 | 97.9519 | 97.7577 | 97.4332 | 94.3845 | 96.4707 | 97.0706 | 97.4161 | 97.3403 | 97.06
Note on G2: If rated voltage is a range, set to the voltage that corresponds to the characterization data.
Note on H2: For multi-output devices, this is the total power for all outputs
Note on L2: This column is set to "N" (no) for laboratory characterization device data sets that are largely redundant with another data set. Multiple instances of the same device under the same voltage conditions were eliminated, but multiple instances of the same device under different voltage conditions were retained.

## Converter Groups
Category | Device Group Description | Output Filename | Converter Models Source File | Power Column Unit | Type | Min Voltage In | Max Voltage In | Min Voltage Out | Max Voltage Out | Min Power Out | Max Power Out | Use Standby | Notes
AC/DC | AC/DC Load-Packaged 0-10W, 0-60VDC out | AC-DC-Load-Packaged-0-10W-0-60VDC | AC-DC Converter Generated Models.mat | W |  | 110 | Inf | 0 | 60 | 0 | 10 | 1
AC/DC | AC/DC Load-Packaged 10-40W, 0-60VDC out | AC-DC-Load-Packaged-10-40W-0-60VDC | AC-DC Converter Generated Models.mat | W |  | 110 | Inf | 0 | 60 | 10 | 40 | 1
AC/DC | AC/DC Load-Packaged 40-120W, 0-60VDC out | AC-DC-Load-Packaged-40-120W-0-60VDC | AC-DC Converter Generated Models.mat | W |  | 110 | Inf | 0 | 60 | 40 | 120 | 1 | Laptops, Monitors, TVs
AC/DC | AC/DC Load-Packaged 120-1000W, 0-60VDC out | AC-DC-Load-Packaged-120-1000W-0-60VDC | AC-DC Converter Generated Models.mat | W |  | 110 | Inf | 0 | 60 | 120 | 1000 | 1 | Desktops, Printers, Copiers, MFDs, (larger) IT Equipment
AC/DC | AC/DC LED Driver 20-100W, 10-60VDC out | AC-DC-LED-20-100W-10-60VDC | AC-DC Converter Generated Models.mat | W | SISO | 110 | Inf | 10 | 60 | 20 | 100 | 1 | LED Drivers
AC/DC | AC/DC Central Rectifier 0-60VDC out | AC-DC-Central-0-60VDC | AC-DC Converter Generated Models.mat | W |  | 110 | Inf | 0 | 60 | 400 | 2000 | 0 | Central AC/DC multichannel converters (e.g. EMerge, PoE)
AC/DC | AC/DC Rectifier for Central Bidirectional Converter ~380VDC out | AC-DC-Central-380VDC | AC-DC Converter Generated Models.mat | W | SISO | 110 | Inf | 60 | 600 | 1000 | Inf | 0 | Central AC/DC converters (rectifier stage of bidirectional converters)
DC/DC | DC/DC Load-Packaged 0-10W, 0-60VDC out | DC-DC-Load-Packaged-0-10W-0-60VDC | DC-DC Converter Generated Models.mat | W |  | 0 | 60 | 0 | 60 | 0 | 10 | 1
DC/DC | DC/DC Load-Packaged 10-40W, 0-60VDC out | DC-DC-Load-Packaged-10-40W-0-60VDC | DC-DC Converter Generated Models.mat | W |  | 0 | 60 | 0 | 60 | 10 | 40 | 1
DC/DC | DC/DC Load-Packaged 40-120W, 0-60VDC out | DC-DC-Load-Packaged-40-120W-0-60VDC | DC-DC Converter Generated Models.mat | W |  | 0 | 60 | 0 | 60 | 40 | 120 | 1 | Laptops, Monitors, TVs
DC/DC | DC/DC Load-Packaged 120-1000W, 0-60VDC out | DC-DC-Load-Packaged-120-1000W-0-60VDC | DC-DC Converter Generated Models.mat | W |  | 0 | 60 | 0 | 60 | 120 | 1000 | 1 | Desktops, Printers, Copiers, MFDs, (larger) IT Equipment
DC/DC | DC/DC LED Driver 20-100W, 10-60VDC out | DC-DC-LED-20-100W-10-60VDC | DC-DC Converter Generated Models.mat | W | SISO | 0 | 60 | 10 | 60 | 20 | 100 | 1 | LED Drivers
DC/DC | DC/DC Central Converter, 380VDC in, 0-60VDC out | DC-DC-Central-0-60VDC | DC-DC Converter Generated Models.mat | W |  | 300 | 600 | 0 | 60 | 400 | Inf | 0 | Central DC/DC step-down converters, including multichannel (e.g. EMerge, PoE)
DC/DC | DC/DC PV MPPT Controller or DC Optimizer | DC-DC-PV-MPPT | DC-DC Converter Generated Models.mat | W |  | 48 | 600 | 48 | 600 | 100 | Inf | 1 | DC/DC converter for PV array: MPPT trackers and DC optimizers
DC/AC | DC/AC PV Inverter (Grid-Tie) | DC-AC-PV-Inverter-110-600VAC | PV Inverter Generated Models.mat | kW |  | 0 | 1000 | 110 | 600 | 0 | Inf | 1 | All PV inverter sizes (assuming actual selection would entail multiple converters)
DC/AC | DC/AC Inverter for Central Bidirectional Converter ~380VDC in | DC-AC-Central-Bidirectional-200-600VAC | Battery Inverter Generated Models.mat | kW |  | 200 | 1000 | 200 | 600 | 1 | Inf | 0 | DC/AC inverter stage for larger bidirectional converters
DC/AC | DC/AC Inverter for Distributed Loads, 400-5000W, 110-250VAC out | DC-AC-Distributed-400-5000W-110-250VAC | Battery Inverter Generated Models.mat | kW |  | 200 | 1000 | 110 | 250 | 0.4 | 5 | 1 | DC/AC inverter for serving distributed AC MELs